## EASY_M Master
Master
Modbus default communication parameters : 8 data bits, paritiy even, 2 stop bits, address 1, 19200 bds. Address and bauds rate can be changed, please see the master documentation
| Read Analog (Function 4) |  |  |  | Write Analog (Function 16)
Status master | Modbus |  |  | Control master | Modbus
| Address | Value |  |  | Address | Value
| 0 | 0 | Stop |  | 0 | 0 | Stop
|  | 1 | Run |  |  | 1 | Run
|  | 2 | Scan |  |  | 3 | fire
|  | 3 | fire |  |  | 3 | fire
|  | 4 | All open slave
Quantity of slave | 1 | 0-128
Quantity error of slave | 2 | 0-128
Fire | 3 | 0-1 | 0 = Fire
EasyBus cycle time | 4 | 0-16000 | [ms]
Firmware version | 5 | 0-1

## EASY-Information
Fire damper | [7 empty] | E = Module error communication
S.T = Slave Type (0=n.c, 4 = Easy-V, 5 = Easy-B 24V, 6 = Easy-B 230V, 7 = Easy-Eco, 8 = Easy-CO2, 9 = Easy-R, 10 = Easy-IO, 11 = Easy-MP)
Retry = Retry counter with the module
E.Counter = Counter of the number error communication with the module
E.Code = Error code of the module
Easybus | modbus RTU |  |  | Easybus | modbus RTU |  | Easybus | modbus RTU
Address |  | Read (bits) |  | Address |  | Read (bits) | Address |  | Read (bits)
|  | E | S.T. |  |  | Retry |  |  | E.Counter
1 | 10 | 7 | 0…6 | 1 | 74 | Slave 1 | 1 | 202 | 0…7
2 |  | 15 | 8…14 | 2 | 75 | Slave 2 | 2 |  | 8…15
3 | 11 | 7 | 0…6 | 3 | 76 | Slave 3 | 3 | 203 | 0…7
4 |  | 15 | 8…14 | 4 | 77 | Slave 4 | 4 |  | 8…15
5 | 12 | 7 | 0…6 | 5 | 78 | Slave 5 | 5 | 204 | 0…7
6 |  | 15 | 8…14 | 6 | 79 | Slave 6 | 6 |  | 8…15
7 | 13 | 7 | 0…6 | 7 | 80 | Slave 7 | 7 | 205 | 0…7
8 |  | 15 | 8…14 | 8 | 81 | Slave 8 | 8 |  | 8…15
9 | 14 | 7 | 0…6 | 9 | 82 | Slave 9 | 9 | 206 | 0…7
10 |  | 15 | 8…14 | 10 | 83 | Slave 10 | 10 |  | 8…15
11 | 15 | 7 | 0…6 | 11 | 84 | Slave 11 | 11 | 207 | 0…7
12 |  | 15 | 8…14 | 12 | 85 | Slave 12 | 12 |  | 8…15
13 | 16 | 7 | 0…6 | 13 | 86 | Slave 13 | 13 | 208 | 0…7
14 |  | 15 | 8…14 | 14 | 87 | Slave 14 | 14 |  | 8…15
15 | 17 | 7 | 0…6 | 15 | 88 | Slave 15 | 15 | 209 | 0…7
16 |  | 15 | 8…14 | 16 | 89 | Slave 16 | 16 |  | 8…15
17 | 18 | 7 | 0…6 | 17 | 90 | Slave 17 | 17 | 210 | 0…7
18 |  | 15 | 8…14 | 18 | 91 | Slave 18 | 18 |  | 8…15
19 | 19 | 7 | 0…6 | 19 | 92 | Slave 19 | 19 | 211 | 0…7
20 |  | 15 | 8…14 | 20 | 93 | Slave 20 | 20 |  | 8…15
21 | 20 | 7 | 0…6 | 21 | 94 | Slave 21 | 21 | 212 | 0…7
22 |  | 15 | 8…14 | 22 | 95 | Slave 22 | 22 |  | 8…15
23 | 21 | 7 | 0…6 | 23 | 96 | Slave 23 | 23 | 213 | 0…7
24 |  | 15 | 8…14 | 24 | 97 | Slave 24 | 24 |  | 8…15
25 | 22 | 7 | 0…6 | 25 | 98 | Slave 25 | 25 | 214 | 0…7
26 |  | 15 | 8…14 | 26 | 99 | Slave 26 | 26 |  | 8…15
27 | 23 | 7 | 0…6 | 27 | 100 | Slave 27 | 27 | 215 | 0…7
28 |  | 15 | 8…14 | 28 | 101 | Slave 28 | 28 |  | 8…15
29 | 24 | 7 | 0…6 | 29 | 102 | Slave 29 | 29 | 216 | 0…7
30 |  | 15 | 8…14 | 30 | 103 | Slave 30 | 30 |  | 8…15
31 | 25 | 7 | 0…6 | 31 | 104 | Slave 31 | 31 | 217 | 0…7
32 |  | 15 | 8…14 | 32 | 105 | Slave 32 | 32 |  | 8…15
33 | 26 | 7 | 0…6 | 33 | 106 | Slave 33 | 33 | 218 | 0…7
34 |  | 15 | 8…14 | 34 | 107 | Slave 34 | 34 |  | 8…15
35 | 27 | 7 | 0…6 | 35 | 108 | Slave 35 | 35 | 219 | 0…7
36 |  | 15 | 8…14 | 36 | 109 | Slave 36 | 36 |  | 8…15
37 | 28 | 7 | 0…6 | 37 | 110 | Slave 37 | 37 | 220 | 0…7
38 |  | 15 | 8…14 | 38 | 111 | Slave 38 | 38 |  | 8…15
39 | 29 | 7 | 0…6 | 39 | 112 | Slave 39 | 39 | 221 | 0…7
40 |  | 15 | 8…14 | 40 | 113 | Slave 40 | 40 |  | 8…15
41 | 30 | 7 | 0…6 | 41 | 114 | Slave 41 | 41 | 222 | 0…7
42 |  | 15 | 8…14 | 42 | 115 | Slave 42 | 42 |  | 8…15
43 | 31 | 7 | 0…6 | 43 | 116 | Slave 43 | 43 | 223 | 0…7
44 |  | 15 | 8…14 | 44 | 117 | Slave 44 | 44 |  | 8…15
45 | 32 | 7 | 0…6 | 45 | 118 | Slave 45 | 45 | 224 | 0…7
46 |  | 15 | 8…14 | 46 | 119 | Slave 46 | 46 |  | 8…15
47 | 33 | 7 | 0…6 | 47 | 120 | Slave 47 | 47 | 225 | 0…7
48 |  | 15 | 8…14 | 48 | 121 | Slave 48 | 48 |  | 8…15
49 | 34 | 7 | 0…6 | 49 | 122 | Slave 49 | 49 | 226 | 0…7
50 |  | 15 | 8…14 | 50 | 123 | Slave 50 | 50 |  | 8…15
51 | 35 | 7 | 0…6 | 51 | 124 | Slave 51 | 51 | 227 | 0…7
52 |  | 15 | 8…14 | 52 | 125 | Slave 52 | 52 |  | 8…15
53 | 36 | 7 | 0…6 | 53 | 126 | Slave 53 | 53 | 228 | 0…7
54 |  | 15 | 8…14 | 54 | 127 | Slave 54 | 54 |  | 8…15
55 | 37 | 7 | 0…6 | 55 | 128 | Slave 55 | 55 | 229 | 0…7
56 |  | 15 | 8…14 | 56 | 129 | Slave 56 | 56 |  | 8…15
57 | 38 | 7 | 0…6 | 57 | 130 | Slave 57 | 57 | 230 | 0…7
58 |  | 15 | 8…14 | 58 | 131 | Slave 58 | 58 |  | 8…15
59 | 39 | 7 | 0…6 | 59 | 132 | Slave 59 | 59 | 231 | 0…7
60 |  | 15 | 8…14 | 60 | 133 | Slave 60 | 60 |  | 8…15
61 | 40 | 7 | 0…6 | 61 | 134 | Slave 61 | 61 | 232 | 0…7
62 |  | 15 | 8…14 | 62 | 135 | Slave 62 | 62 |  | 8…15
63 | 41 | 7 | 0…6 | 63 | 136 | Slave 63 | 63 | 233 | 0…7
64 |  | 15 | 8…14 | 64 | 137 | Slave 64 | 64 |  | 8…15
65 | 42 | 7 | 0…6 | 65 | 138 | Slave 65 | 65 | 234 | 0…7
66 |  | 15 | 8…14 | 66 | 139 | Slave 66 | 66 |  | 8…15
67 | 43 | 7 | 0…6 | 67 | 140 | Slave 67 | 67 | 235 | 0…7
68 |  | 15 | 8…14 | 68 | 141 | Slave 68 | 68 |  | 8…15
69 | 44 | 7 | 0…6 | 69 | 142 | Slave 69 | 69 | 236 | 0…7
70 |  | 15 | 8…14 | 70 | 143 | Slave 70 | 70 |  | 8…15
71 | 45 | 7 | 0…6 | 71 | 144 | Slave 71 | 71 | 237 | 0…7
72 |  | 15 | 8…14 | 72 | 145 | Slave 72 | 72 |  | 8…15
73 | 46 | 7 | 0…6 | 73 | 146 | Slave 73 | 73 | 238 | 0…7
74 |  | 15 | 8…14 | 74 | 147 | Slave 74 | 74 |  | 8…15
75 | 47 | 7 | 0…6 | 75 | 148 | Slave 75 | 75 | 239 | 0…7
76 |  | 15 | 8…14 | 76 | 149 | Slave 76 | 76 |  | 8…15
77 | 48 | 7 | 0…6 | 77 | 150 | Slave 77 | 77 | 240 | 0…7
78 |  | 15 | 8…14 | 78 | 151 | Slave 78 | 78 |  | 8…15
79 | 49 | 7 | 0…6 | 79 | 152 | Slave 79 | 79 | 241 | 0…7
80 |  | 15 | 8…14 | 80 | 153 | Slave 80 | 80 |  | 8…15
81 | 50 | 7 | 0…6 | 81 | 154 | Slave 81 | 81 | 242 | 0…7
82 |  | 15 | 8…14 | 82 | 155 | Slave 82 | 82 |  | 8…15
83 | 51 | 7 | 0…6 | 83 | 156 | Slave 83 | 83 | 243 | 0…7
84 |  | 15 | 8…14 | 84 | 157 | Slave 84 | 84 |  | 8…15
85 | 52 | 7 | 0…6 | 85 | 158 | Slave 85 | 85 | 244 | 0…7
86 |  | 15 | 8…14 | 86 | 159 | Slave 86 | 86 |  | 8…15
87 | 53 | 7 | 0…6 | 87 | 160 | Slave 87 | 87 | 245 | 0…7
88 |  | 15 | 8…14 | 88 | 161 | Slave 88 | 88 |  | 8…15
89 | 54 | 7 | 0…6 | 89 | 162 | Slave 89 | 89 | 246 | 0…7
90 |  | 15 | 8…14 | 90 | 163 | Slave 90 | 90 |  | 8…15
91 | 55 | 7 | 0…6 | 91 | 164 | Slave 91 | 91 | 247 | 0…7
92 |  | 15 | 8…14 | 92 | 165 | Slave 92 | 92 |  | 8…15
93 | 56 | 7 | 0…6 | 93 | 166 | Slave 93 | 93 | 248 | 0…7
94 |  | 15 | 8…14 | 94 | 167 | Slave 94 | 94 |  | 8…15
95 | 57 | 7 | 0…6 | 95 | 168 | Slave 95 | 95 | 249 | 0…7
96 |  | 15 | 8…14 | 96 | 169 | Slave 96 | 96 |  | 8…15
97 | 58 | 7 | 0…6 | 97 | 170 | Slave 97 | 97 | 250 | 0…7
98 |  | 15 | 8…14 | 98 | 171 | Slave 98 | 98 |  | 8…15
99 | 59 | 7 | 0…6 | 99 | 172 | Slave 99 | 99 | 251 | 0…7
100 |  | 15 | 8…14 | 100 | 173 | Slave 100 | 100 |  | 8…15
101 | 60 | 7 | 0…6 | 101 | 174 | Slave 101 | 101 | 252 | 0…7
102 |  | 15 | 8…14 | 102 | 175 | Slave 102 | 102 |  | 8…15
103 | 61 | 7 | 0…6 | 103 | 176 | Slave 103 | 103 | 253 | 0…7
104 |  | 15 | 8…14 | 104 | 177 | Slave 104 | 104 |  | 8…15
105 | 62 | 7 | 0…6 | 105 | 178 | Slave 105 | 105 | 254 | 0…7
106 |  | 15 | 8…14 | 106 | 179 | Slave 106 | 106 |  | 8…15
107 | 63 | 7 | 0…6 | 107 | 180 | Slave 107 | 107 | 255 | 0…7
108 |  | 15 | 8…14 | 108 | 181 | Slave 108 | 108 |  | 8…15
109 | 64 | 7 | 0…6 | 109 | 182 | Slave 109 | 109 | 256 | 0…7
110 |  | 15 | 8…14 | 110 | 183 | Slave 110 | 110 |  | 8…15
111 | 65 | 7 | 0…6 | 111 | 184 | Slave 111 | 111 | 257 | 0…7
112 |  | 15 | 8…14 | 112 | 185 | Slave 112 | 112 |  | 8…15
113 | 66 | 7 | 0…6 | 113 | 186 | Slave 113 | 113 | 258 | 0…7
114 |  | 15 | 8…14 | 114 | 187 | Slave 114 | 114 |  | 8…15
115 | 67 | 7 | 0…6 | 115 | 188 | Slave 115 | 115 | 259 | 0…7
116 |  | 15 | 8…14 | 116 | 189 | Slave 116 | 116 |  | 8…15
117 | 68 | 7 | 0…6 | 117 | 190 | Slave 117 | 117 | 260 | 0…7
118 |  | 15 | 8…14 | 118 | 191 | Slave 118 | 118 |  | 8…15
119 | 69 | 7 | 0…6 | 119 | 192 | Slave 119 | 119 | 261 | 0…7
120 |  | 15 | 8…14 | 120 | 193 | Slave 120 | 120 |  | 8…15
121 | 70 | 7 | 0…6 | 121 | 194 | Slave 121 | 121 | 262 | 0…7
122 |  | 15 | 8…14 | 122 | 195 | Slave 122 | 122 |  | 8…15
123 | 71 | 7 | 0…6 | 123 | 196 | Slave 123 | 123 | 263 | 0…7
124 |  | 15 | 8…14 | 124 | 197 | Slave 124 | 124 |  | 8…15
125 | 72 | 7 | 0…6 | 125 | 198 | Slave 125 | 125 | 264 | 0…7
126 |  | 15 | 8…14 | 126 | 199 | Slave 126 | 126 |  | 8…15
127 | 73 | 7 | 0…6 | 127 | 200 | Slave 127 | 127 | 265 | 0…7
128 |  | 15 | 8…14 | 128 | 201 | Slave 128 | 128 |  | 8…15

## EASY-B CCF
Information | [8 empty] | E = Error
C = Close
O = Open
F = Smoke detector
S = Control fire damper
Easybus | modbus RTU |  |  |  |  | Easybus | modbus RTU
Address |  | Read (bits) |  |  |  | Address |  | Write (bits)
|  | F | O | C | E |  |  | S
1 | 300 | 3 | 2 | 1 | 0 | 1 | 300 | 0
2 |  | 7 | 6 | 5 | 4 | 2 |  | 1
3 |  | 11 | 10 | 9 | 8 | 3 |  | 2
4 |  | 15 | 14 | 13 | 12 | 4 |  | 3
5 | 301 | 3 | 2 | 1 | 0 | 5 |  | 4
6 |  | 7 | 6 | 5 | 4 | 6 |  | 5
7 |  | 11 | 10 | 9 | 8 | 7 |  | 6
8 |  | 15 | 14 | 13 | 12 | 8 |  | 7
9 | 302 | 3 | 2 | 1 | 0 | 9 |  | 8
10 |  | 7 | 6 | 5 | 4 | 10 |  | 9
11 |  | 11 | 10 | 9 | 8 | 11 |  | 10
12 |  | 15 | 14 | 13 | 12 | 12 |  | 11
13 | 303 | 3 | 2 | 1 | 0 | 13 |  | 12
14 |  | 7 | 6 | 5 | 4 | 14 |  | 13
15 |  | 11 | 10 | 9 | 8 | 15 |  | 14
16 |  | 15 | 14 | 13 | 12 | 16 |  | 15
17 | 304 | 3 | 2 | 1 | 0 | 17 | 301 | 0
18 |  | 7 | 6 | 5 | 4 | 18 |  | 1
19 |  | 11 | 10 | 9 | 8 | 19 |  | 2
20 |  | 15 | 14 | 13 | 12 | 20 |  | 3
21 | 305 | 3 | 2 | 1 | 0 | 21 |  | 4
22 |  | 7 | 6 | 5 | 4 | 22 |  | 5
23 |  | 11 | 10 | 9 | 8 | 23 |  | 6
24 |  | 15 | 14 | 13 | 12 | 24 |  | 7
25 | 306 | 3 | 2 | 1 | 0 | 25 |  | 8
26 |  | 7 | 6 | 5 | 4 | 26 |  | 9
27 |  | 11 | 10 | 9 | 8 | 27 |  | 10
28 |  | 15 | 14 | 13 | 12 | 28 |  | 11
29 | 307 | 3 | 2 | 1 | 0 | 29 |  | 12
30 |  | 7 | 6 | 5 | 4 | 30 |  | 13
31 |  | 11 | 10 | 9 | 8 | 31 |  | 14
32 |  | 15 | 14 | 13 | 12 | 32 |  | 15
33 | 308 | 3 | 2 | 1 | 0 | 33 | 302 | 0
34 |  | 7 | 6 | 5 | 4 | 34 |  | 1
35 |  | 11 | 10 | 9 | 8 | 35 |  | 2
36 |  | 15 | 14 | 13 | 12 | 36 |  | 3
37 | 309 | 3 | 2 | 1 | 0 | 37 |  | 4
38 |  | 7 | 6 | 5 | 4 | 38 |  | 5
39 |  | 11 | 10 | 9 | 8 | 39 |  | 6
40 |  | 15 | 14 | 13 | 12 | 40 |  | 7
41 | 310 | 3 | 2 | 1 | 0 | 41 |  | 8
42 |  | 7 | 6 | 5 | 4 | 42 |  | 9
43 |  | 11 | 10 | 9 | 8 | 43 |  | 10
44 |  | 15 | 14 | 13 | 12 | 44 |  | 11
45 | 311 | 3 | 2 | 1 | 0 | 45 |  | 12
46 |  | 7 | 6 | 5 | 4 | 46 |  | 13
47 |  | 11 | 10 | 9 | 8 | 47 |  | 14
48 |  | 15 | 14 | 13 | 12 | 48 |  | 15
49 | 312 | 3 | 2 | 1 | 0 | 49 | 303 | 0
50 |  | 7 | 6 | 5 | 4 | 50 |  | 1
51 |  | 11 | 10 | 9 | 8 | 51 |  | 2
52 |  | 15 | 14 | 13 | 12 | 52 |  | 3
53 | 313 | 3 | 2 | 1 | 0 | 53 |  | 4
54 |  | 7 | 6 | 5 | 4 | 54 |  | 5
55 |  | 11 | 10 | 9 | 8 | 55 |  | 6
56 |  | 15 | 14 | 13 | 12 | 56 |  | 7
57 | 314 | 3 | 2 | 1 | 0 | 57 |  | 8
58 |  | 7 | 6 | 5 | 4 | 58 |  | 9
59 |  | 11 | 10 | 9 | 8 | 59 |  | 10
60 |  | 15 | 14 | 13 | 12 | 60 |  | 11
61 | 315 | 3 | 2 | 1 | 0 | 61 |  | 12
62 |  | 7 | 6 | 5 | 4 | 62 |  | 13
63 |  | 11 | 10 | 9 | 8 | 63 |  | 14
64 |  | 15 | 14 | 13 | 12 | 64 |  | 15
65 | 316 | 3 | 2 | 1 | 0 | 65 | 304 | 0
66 |  | 7 | 6 | 5 | 4 | 66 |  | 1
67 |  | 11 | 10 | 9 | 8 | 67 |  | 2
68 |  | 15 | 14 | 13 | 12 | 68 |  | 3
69 | 317 | 3 | 2 | 1 | 0 | 69 |  | 4
70 |  | 7 | 6 | 5 | 4 | 70 |  | 5
71 |  | 11 | 10 | 9 | 8 | 71 |  | 6
72 |  | 15 | 14 | 13 | 12 | 72 |  | 7
73 | 318 | 3 | 2 | 1 | 0 | 73 |  | 8
74 |  | 7 | 6 | 5 | 4 | 74 |  | 9
75 |  | 11 | 10 | 9 | 8 | 75 |  | 10
76 |  | 15 | 14 | 13 | 12 | 76 |  | 11
77 | 319 | 3 | 2 | 1 | 0 | 77 |  | 12
78 |  | 7 | 6 | 5 | 4 | 78 |  | 13
79 |  | 11 | 10 | 9 | 8 | 79 |  | 14
80 |  | 15 | 14 | 13 | 12 | 80 |  | 15
81 | 320 | 3 | 2 | 1 | 0 | 81 | 305 | 0
82 |  | 7 | 6 | 5 | 4 | 82 |  | 1
83 |  | 11 | 10 | 9 | 8 | 83 |  | 2
84 |  | 15 | 14 | 13 | 12 | 84 |  | 3
85 | 321 | 3 | 2 | 1 | 0 | 85 |  | 4
86 |  | 7 | 6 | 5 | 4 | 86 |  | 5
87 |  | 11 | 10 | 9 | 8 | 87 |  | 6
88 |  | 15 | 14 | 13 | 12 | 88 |  | 7
89 | 322 | 3 | 2 | 1 | 0 | 89 |  | 8
90 |  | 7 | 6 | 5 | 4 | 90 |  | 9
91 |  | 11 | 10 | 9 | 8 | 91 |  | 10
92 |  | 15 | 14 | 13 | 12 | 92 |  | 11
93 | 323 | 3 | 2 | 1 | 0 | 93 |  | 12
94 |  | 7 | 6 | 5 | 4 | 94 |  | 13
95 |  | 11 | 10 | 9 | 8 | 95 |  | 14
96 |  | 15 | 14 | 13 | 12 | 96 |  | 15
97 | 324 | 3 | 2 | 1 | 0 | 97 | 306 | 0
98 |  | 7 | 6 | 5 | 4 | 98 |  | 1
99 |  | 11 | 10 | 9 | 8 | 99 |  | 2
100 |  | 15 | 14 | 13 | 12 | 100 |  | 3
101 | 325 | 3 | 2 | 1 | 0 | 101 |  | 4
102 |  | 7 | 6 | 5 | 4 | 102 |  | 5
103 |  | 11 | 10 | 9 | 8 | 103 |  | 6
104 |  | 15 | 14 | 13 | 12 | 104 |  | 7
105 | 326 | 3 | 2 | 1 | 0 | 105 |  | 8
106 |  | 7 | 6 | 5 | 4 | 106 |  | 9
107 |  | 11 | 10 | 9 | 8 | 107 |  | 10
108 |  | 15 | 14 | 13 | 12 | 108 |  | 11
109 | 327 | 3 | 2 | 1 | 0 | 109 |  | 12
110 |  | 7 | 6 | 5 | 4 | 110 |  | 13
111 |  | 11 | 10 | 9 | 8 | 111 |  | 14
112 |  | 15 | 14 | 13 | 12 | 112 |  | 15
113 | 328 | 3 | 2 | 1 | 0 | 113 | 307 | 0
114 |  | 7 | 6 | 5 | 4 | 114 |  | 1
115 |  | 11 | 10 | 9 | 8 | 115 |  | 2
116 |  | 15 | 14 | 13 | 12 | 116 |  | 3
117 | 329 | 3 | 2 | 1 | 0 | 117 |  | 4
118 |  | 7 | 6 | 5 | 4 | 118 |  | 5
119 |  | 11 | 10 | 9 | 8 | 119 |  | 6
120 |  | 15 | 14 | 13 | 12 | 120 |  | 7
121 | 330 | 3 | 2 | 1 | 0 | 121 |  | 8
122 |  | 7 | 6 | 5 | 4 | 122 |  | 9
123 |  | 11 | 10 | 9 | 8 | 123 |  | 10
124 |  | 15 | 14 | 13 | 12 | 124 |  | 11
125 | 331 | 3 | 2 | 1 | 0 | 125 |  | 12
126 |  | 7 | 6 | 5 | 4 | 126 |  | 13
127 |  | 11 | 10 | 9 | 8 | 127 |  | 14
128 |  | 15 | 14 | 13 | 12 | 128 |  | 15

## EASY-V VAV
VAV
Easybus | modbus RTU |  | Easybus | modbus RTU |  | Easybus | modbus RTU |  | Easybus | modbus RTU
Address |  | Read VAV | Address |  | Write VAV | Address |  | Read sensor | Address |  | Read (bits)
|  | 0-1000 |  |  | 0-1000 |  |  | 0-1000 |  |  | Module error communication
1 | 460 | VAV N°1 | 1 | 460 | VAV N°1 | 1 | 716 | Probe N°1 | 1 | 300 | 0
| 461 | VAV N°2 |  | 461 | VAV N°2 |  | 717 | Probe N°2 | 2 |  | 4
2 | 462 | VAV N°1 | 2 | 462 | VAV N°1 | 2 | 718 | Probe N°1 | 3 |  | 8
| 463 | VAV N°2 |  | 463 | VAV N°2 |  | 719 | Probe N°2 | 4 |  | 12
3 | 464 | VAV N°1 | 3 | 464 | VAV N°1 | 3 | 720 | Probe N°1 | 5 | 301 | 0
| 465 | VAV N°2 |  | 465 | VAV N°2 |  | 721 | Probe N°2 | 6 |  | 4
4 | 466 | VAV N°1 | 4 | 466 | VAV N°1 | 4 | 722 | Probe N°1 | 7 |  | 8
| 467 | VAV N°2 |  | 467 | VAV N°2 |  | 723 | Probe N°2 | 8 |  | 12
5 | 468 | VAV N°1 | 5 | 468 | VAV N°1 | 5 | 724 | Probe N°1 | 9 | 302 | 0
| 469 | VAV N°2 |  | 469 | VAV N°2 |  | 725 | Probe N°2 | 10 |  | 4
6 | 470 | VAV N°1 | 6 | 470 | VAV N°1 | 6 | 726 | Probe N°1 | 11 |  | 8
| 471 | VAV N°2 |  | 471 | VAV N°2 |  | 727 | Probe N°2 | 12 |  | 12
7 | 472 | VAV N°1 | 7 | 472 | VAV N°1 | 7 | 728 | Probe N°1 | 13 | 303 | 0
| 473 | VAV N°2 |  | 473 | VAV N°2 |  | 729 | Probe N°2 | 14 |  | 4
8 | 474 | VAV N°1 | 8 | 474 | VAV N°1 | 8 | 730 | Probe N°1 | 15 |  | 8
| 475 | VAV N°2 |  | 475 | VAV N°2 |  | 731 | Probe N°2 | 16 |  | 12
9 | 476 | VAV N°1 | 9 | 476 | VAV N°1 | 9 | 732 | Probe N°1 | 17 | 304 | 0
| 477 | VAV N°2 |  | 477 | VAV N°2 |  | 733 | Probe N°2 | 18 |  | 4
10 | 478 | VAV N°1 | 10 | 478 | VAV N°1 | 10 | 734 | Probe N°1 | 19 |  | 8
| 479 | VAV N°2 |  | 479 | VAV N°2 |  | 735 | Probe N°2 | 20 |  | 12
11 | 480 | VAV N°1 | 11 | 480 | VAV N°1 | 11 | 736 | Probe N°1 | 21 | 305 | 0
| 481 | VAV N°2 |  | 481 | VAV N°2 |  | 737 | Probe N°2 | 22 |  | 4
12 | 482 | VAV N°1 | 12 | 482 | VAV N°1 | 12 | 738 | Probe N°1 | 23 |  | 8
| 483 | VAV N°2 |  | 483 | VAV N°2 |  | 739 | Probe N°2 | 24 |  | 12
13 | 484 | VAV N°1 | 13 | 484 | VAV N°1 | 13 | 740 | Probe N°1 | 25 | 306 | 0
| 485 | VAV N°2 |  | 485 | VAV N°2 |  | 741 | Probe N°2 | 26 |  | 4
14 | 486 | VAV N°1 | 14 | 486 | VAV N°1 | 14 | 742 | Probe N°1 | 27 |  | 8
| 487 | VAV N°2 |  | 487 | VAV N°2 |  | 743 | Probe N°2 | 28 |  | 12
15 | 488 | VAV N°1 | 15 | 488 | VAV N°1 | 15 | 744 | Probe N°1 | 29 | 307 | 0
| 489 | VAV N°2 |  | 489 | VAV N°2 |  | 745 | Probe N°2 | 30 |  | 4
16 | 490 | VAV N°1 | 16 | 490 | VAV N°1 | 16 | 746 | Probe N°1 | 31 |  | 8
| 491 | VAV N°2 |  | 491 | VAV N°2 |  | 747 | Probe N°2 | 32 |  | 12
17 | 492 | VAV N°1 | 17 | 492 | VAV N°1 | 17 | 748 | Probe N°1 | 33 | 308 | 0
| 493 | VAV N°2 |  | 493 | VAV N°2 |  | 749 | Probe N°2 | 34 |  | 4
18 | 494 | VAV N°1 | 18 | 494 | VAV N°1 | 18 | 750 | Probe N°1 | 35 |  | 8
| 495 | VAV N°2 |  | 495 | VAV N°2 |  | 751 | Probe N°2 | 36 |  | 12
19 | 496 | VAV N°1 | 19 | 496 | VAV N°1 | 19 | 752 | Probe N°1 | 37 | 309 | 0
| 497 | VAV N°2 |  | 497 | VAV N°2 |  | 753 | Probe N°2 | 38 |  | 4
20 | 498 | VAV N°1 | 20 | 498 | VAV N°1 | 20 | 754 | Probe N°1 | 39 |  | 8
| 499 | VAV N°2 |  | 499 | VAV N°2 |  | 755 | Probe N°2 | 40 |  | 12
21 | 500 | VAV N°1 | 21 | 500 | VAV N°1 | 21 | 756 | Probe N°1 | 41 | 310 | 0
| 501 | VAV N°2 |  | 501 | VAV N°2 |  | 757 | Probe N°2 | 42 |  | 4
22 | 502 | VAV N°1 | 22 | 502 | VAV N°1 | 22 | 758 | Probe N°1 | 43 |  | 8
| 503 | VAV N°2 |  | 503 | VAV N°2 |  | 759 | Probe N°2 | 44 |  | 12
23 | 504 | VAV N°1 | 23 | 504 | VAV N°1 | 23 | 760 | Probe N°1 | 45 | 311 | 0
| 505 | VAV N°2 |  | 505 | VAV N°2 |  | 761 | Probe N°2 | 46 |  | 4
24 | 506 | VAV N°1 | 24 | 506 | VAV N°1 | 24 | 762 | Probe N°1 | 47 |  | 8
| 507 | VAV N°2 |  | 507 | VAV N°2 |  | 763 | Probe N°2 | 48 |  | 12
25 | 508 | VAV N°1 | 25 | 508 | VAV N°1 | 25 | 764 | Probe N°1 | 49 | 312 | 0
| 509 | VAV N°2 |  | 509 | VAV N°2 |  | 765 | Probe N°2 | 50 |  | 4
26 | 510 | VAV N°1 | 26 | 510 | VAV N°1 | 26 | 766 | Probe N°1 | 51 |  | 8
| 511 | VAV N°2 |  | 511 | VAV N°2 |  | 767 | Probe N°2 | 52 |  | 12
27 | 512 | VAV N°1 | 27 | 512 | VAV N°1 | 27 | 768 | Probe N°1 | 53 | 313 | 0
| 513 | VAV N°2 |  | 513 | VAV N°2 |  | 769 | Probe N°2 | 54 |  | 4
28 | 514 | VAV N°1 | 28 | 514 | VAV N°1 | 28 | 770 | Probe N°1 | 55 |  | 8
| 515 | VAV N°2 |  | 515 | VAV N°2 |  | 771 | Probe N°2 | 56 |  | 12
29 | 516 | VAV N°1 | 29 | 516 | VAV N°1 | 29 | 772 | Probe N°1 | 57 | 314 | 0
| 517 | VAV N°2 |  | 517 | VAV N°2 |  | 773 | Probe N°2 | 58 |  | 4
30 | 518 | VAV N°1 | 30 | 518 | VAV N°1 | 30 | 774 | Probe N°1 | 59 |  | 8
| 519 | VAV N°2 |  | 519 | VAV N°2 |  | 775 | Probe N°2 | 60 |  | 12
31 | 520 | VAV N°1 | 31 | 520 | VAV N°1 | 31 | 776 | Probe N°1 | 61 | 315 | 0
| 521 | VAV N°2 |  | 521 | VAV N°2 |  | 777 | Probe N°2 | 62 |  | 4
32 | 522 | VAV N°1 | 32 | 522 | VAV N°1 | 32 | 778 | Probe N°1 | 63 |  | 8
| 523 | VAV N°2 |  | 523 | VAV N°2 |  | 779 | Probe N°2 | 64 |  | 12
33 | 524 | VAV N°1 | 33 | 524 | VAV N°1 | 33 | 780 | Probe N°1 | 65 | 316 | 0
| 525 | VAV N°2 |  | 525 | VAV N°2 |  | 781 | Probe N°2 | 66 |  | 4
34 | 526 | VAV N°1 | 34 | 526 | VAV N°1 | 34 | 782 | Probe N°1 | 67 |  | 8
| 527 | VAV N°2 |  | 527 | VAV N°2 |  | 783 | Probe N°2 | 68 |  | 12
35 | 528 | VAV N°1 | 35 | 528 | VAV N°1 | 35 | 784 | Probe N°1 | 69 | 317 | 0
| 529 | VAV N°2 |  | 529 | VAV N°2 |  | 785 | Probe N°2 | 70 |  | 4
36 | 530 | VAV N°1 | 36 | 530 | VAV N°1 | 36 | 786 | Probe N°1 | 71 |  | 8
| 531 | VAV N°2 |  | 531 | VAV N°2 |  | 787 | Probe N°2 | 72 |  | 12
37 | 532 | VAV N°1 | 37 | 532 | VAV N°1 | 37 | 788 | Probe N°1 | 73 | 318 | 0
| 533 | VAV N°2 |  | 533 | VAV N°2 |  | 789 | Probe N°2 | 74 |  | 4
38 | 534 | VAV N°1 | 38 | 534 | VAV N°1 | 38 | 790 | Probe N°1 | 75 |  | 8
| 535 | VAV N°2 |  | 535 | VAV N°2 |  | 791 | Probe N°2 | 76 |  | 12
39 | 536 | VAV N°1 | 39 | 536 | VAV N°1 | 39 | 792 | Probe N°1 | 77 | 319 | 0
| 537 | VAV N°2 |  | 537 | VAV N°2 |  | 793 | Probe N°2 | 78 |  | 4
40 | 538 | VAV N°1 | 40 | 538 | VAV N°1 | 40 | 794 | Probe N°1 | 79 |  | 8
| 539 | VAV N°2 |  | 539 | VAV N°2 |  | 795 | Probe N°2 | 80 |  | 12
41 | 540 | VAV N°1 | 41 | 540 | VAV N°1 | 41 | 796 | Probe N°1 | 81 | 320 | 0
| 541 | VAV N°2 |  | 541 | VAV N°2 |  | 797 | Probe N°2 | 82 |  | 4
42 | 542 | VAV N°1 | 42 | 542 | VAV N°1 | 42 | 798 | Probe N°1 | 83 |  | 8
| 543 | VAV N°2 |  | 543 | VAV N°2 |  | 799 | Probe N°2 | 84 |  | 12
43 | 544 | VAV N°1 | 43 | 544 | VAV N°1 | 43 | 800 | Probe N°1 | 85 | 321 | 0
| 545 | VAV N°2 |  | 545 | VAV N°2 |  | 801 | Probe N°2 | 86 |  | 4
44 | 546 | VAV N°1 | 44 | 546 | VAV N°1 | 44 | 802 | Probe N°1 | 87 |  | 8
| 547 | VAV N°2 |  | 547 | VAV N°2 |  | 803 | Probe N°2 | 88 |  | 12
45 | 548 | VAV N°1 | 45 | 548 | VAV N°1 | 45 | 804 | Probe N°1 | 89 | 322 | 0
| 549 | VAV N°2 |  | 549 | VAV N°2 |  | 805 | Probe N°2 | 90 |  | 4
46 | 550 | VAV N°1 | 46 | 550 | VAV N°1 | 46 | 806 | Probe N°1 | 91 |  | 8
| 551 | VAV N°2 |  | 551 | VAV N°2 |  | 807 | Probe N°2 | 92 |  | 12
47 | 552 | VAV N°1 | 47 | 552 | VAV N°1 | 47 | 808 | Probe N°1 | 93 | 323 | 0
| 553 | VAV N°2 |  | 553 | VAV N°2 |  | 809 | Probe N°2 | 94 |  | 4
48 | 554 | VAV N°1 | 48 | 554 | VAV N°1 | 48 | 810 | Probe N°1 | 95 |  | 8
| 555 | VAV N°2 |  | 555 | VAV N°2 |  | 811 | Probe N°2 | 96 |  | 12
49 | 556 | VAV N°1 | 49 | 556 | VAV N°1 | 49 | 812 | Probe N°1 | 97 | 324 | 0
| 557 | VAV N°2 |  | 557 | VAV N°2 |  | 813 | Probe N°2 | 98 |  | 4
50 | 558 | VAV N°1 | 50 | 558 | VAV N°1 | 50 | 814 | Probe N°1 | 99 |  | 8
| 559 | VAV N°2 |  | 559 | VAV N°2 |  | 815 | Probe N°2 | 100 |  | 12
51 | 560 | VAV N°1 | 51 | 560 | VAV N°1 | 51 | 816 | Probe N°1 | 101 | 325 | 0
| 561 | VAV N°2 |  | 561 | VAV N°2 |  | 817 | Probe N°2 | 102 |  | 4
52 | 562 | VAV N°1 | 52 | 562 | VAV N°1 | 52 | 818 | Probe N°1 | 103 |  | 8
| 563 | VAV N°2 |  | 563 | VAV N°2 |  | 819 | Probe N°2 | 104 |  | 12
53 | 564 | VAV N°1 | 53 | 564 | VAV N°1 | 53 | 820 | Probe N°1 | 105 | 326 | 0
| 565 | VAV N°2 |  | 565 | VAV N°2 |  | 821 | Probe N°2 | 106 |  | 4
54 | 566 | VAV N°1 | 54 | 566 | VAV N°1 | 54 | 822 | Probe N°1 | 107 |  | 8
| 567 | VAV N°2 |  | 567 | VAV N°2 |  | 823 | Probe N°2 | 108 |  | 12
55 | 568 | VAV N°1 | 55 | 568 | VAV N°1 | 55 | 824 | Probe N°1 | 109 | 327 | 0
| 569 | VAV N°2 |  | 569 | VAV N°2 |  | 825 | Probe N°2 | 110 |  | 4
56 | 570 | VAV N°1 | 56 | 570 | VAV N°1 | 56 | 826 | Probe N°1 | 111 |  | 8
| 571 | VAV N°2 |  | 571 | VAV N°2 |  | 827 | Probe N°2 | 112 |  | 12
57 | 572 | VAV N°1 | 57 | 572 | VAV N°1 | 57 | 828 | Probe N°1 | 113 | 328 | 0
| 573 | VAV N°2 |  | 573 | VAV N°2 |  | 829 | Probe N°2 | 114 |  | 4
58 | 574 | VAV N°1 | 58 | 574 | VAV N°1 | 58 | 830 | Probe N°1 | 115 |  | 8
| 575 | VAV N°2 |  | 575 | VAV N°2 |  | 831 | Probe N°2 | 116 |  | 12
59 | 576 | VAV N°1 | 59 | 576 | VAV N°1 | 59 | 832 | Probe N°1 | 117 | 329 | 0
| 577 | VAV N°2 |  | 577 | VAV N°2 |  | 833 | Probe N°2 | 118 |  | 4
60 | 578 | VAV N°1 | 60 | 578 | VAV N°1 | 60 | 834 | Probe N°1 | 119 |  | 8
| 579 | VAV N°2 |  | 579 | VAV N°2 |  | 835 | Probe N°2 | 120 |  | 12
61 | 580 | VAV N°1 | 61 | 580 | VAV N°1 | 61 | 836 | Probe N°1 | 121 | 330 | 0
| 581 | VAV N°2 |  | 581 | VAV N°2 |  | 837 | Probe N°2 | 122 |  | 4
62 | 582 | VAV N°1 | 62 | 582 | VAV N°1 | 62 | 838 | Probe N°1 | 123 |  | 8
| 583 | VAV N°2 |  | 583 | VAV N°2 |  | 839 | Probe N°2 | 124 |  | 12
63 | 584 | VAV N°1 | 63 | 584 | VAV N°1 | 63 | 840 | Probe N°1 | 125 | 331 | 0
| 585 | VAV N°2 |  | 585 | VAV N°2 |  | 841 | Probe N°2 | 126 |  | 4
64 | 586 | VAV N°1 | 64 | 586 | VAV N°1 | 64 | 842 | Probe N°1 | 127 |  | 8
| 587 | VAV N°2 |  | 587 | VAV N°2 |  | 843 | Probe N°2 | 128 |  | 12
65 | 588 | VAV N°1 | 65 | 588 | VAV N°1 | 65 | 844 | Probe N°1
| 589 | VAV N°2 |  | 589 | VAV N°2 |  | 845 | Probe N°2
66 | 590 | VAV N°1 | 66 | 590 | VAV N°1 | 66 | 846 | Probe N°1
| 591 | VAV N°2 |  | 591 | VAV N°2 |  | 847 | Probe N°2
67 | 592 | VAV N°1 | 67 | 592 | VAV N°1 | 67 | 848 | Probe N°1
| 593 | VAV N°2 |  | 593 | VAV N°2 |  | 849 | Probe N°2
68 | 594 | VAV N°1 | 68 | 594 | VAV N°1 | 68 | 850 | Probe N°1
| 595 | VAV N°2 |  | 595 | VAV N°2 |  | 851 | Probe N°2
69 | 596 | VAV N°1 | 69 | 596 | VAV N°1 | 69 | 852 | Probe N°1
| 597 | VAV N°2 |  | 597 | VAV N°2 |  | 853 | Probe N°2
70 | 598 | VAV N°1 | 70 | 598 | VAV N°1 | 70 | 854 | Probe N°1
| 599 | VAV N°2 |  | 599 | VAV N°2 |  | 855 | Probe N°2
71 | 600 | VAV N°1 | 71 | 600 | VAV N°1 | 71 | 856 | Probe N°1
| 601 | VAV N°2 |  | 601 | VAV N°2 |  | 857 | Probe N°2
72 | 602 | VAV N°1 | 72 | 602 | VAV N°1 | 72 | 858 | Probe N°1
| 603 | VAV N°2 |  | 603 | VAV N°2 |  | 859 | Probe N°2
73 | 604 | VAV N°1 | 73 | 604 | VAV N°1 | 73 | 860 | Probe N°1
| 605 | VAV N°2 |  | 605 | VAV N°2 |  | 861 | Probe N°2
74 | 606 | VAV N°1 | 74 | 606 | VAV N°1 | 74 | 862 | Probe N°1
| 607 | VAV N°2 |  | 607 | VAV N°2 |  | 863 | Probe N°2
75 | 608 | VAV N°1 | 75 | 608 | VAV N°1 | 75 | 864 | Probe N°1
| 609 | VAV N°2 |  | 609 | VAV N°2 |  | 865 | Probe N°2
76 | 610 | VAV N°1 | 76 | 610 | VAV N°1 | 76 | 866 | Probe N°1
| 611 | VAV N°2 |  | 611 | VAV N°2 |  | 867 | Probe N°2
77 | 612 | VAV N°1 | 77 | 612 | VAV N°1 | 77 | 868 | Probe N°1
| 613 | VAV N°2 |  | 613 | VAV N°2 |  | 869 | Probe N°2
78 | 614 | VAV N°1 | 78 | 614 | VAV N°1 | 78 | 870 | Probe N°1
| 615 | VAV N°2 |  | 615 | VAV N°2 |  | 871 | Probe N°2
79 | 616 | VAV N°1 | 79 | 616 | VAV N°1 | 79 | 872 | Probe N°1
| 617 | VAV N°2 |  | 617 | VAV N°2 |  | 873 | Probe N°2
80 | 618 | VAV N°1 | 80 | 618 | VAV N°1 | 80 | 874 | Probe N°1
| 619 | VAV N°2 |  | 619 | VAV N°2 |  | 875 | Probe N°2
81 | 620 | VAV N°1 | 81 | 620 | VAV N°1 | 81 | 876 | Probe N°1
| 621 | VAV N°2 |  | 621 | VAV N°2 |  | 877 | Probe N°2
82 | 622 | VAV N°1 | 82 | 622 | VAV N°1 | 82 | 878 | Probe N°1
| 623 | VAV N°2 |  | 623 | VAV N°2 |  | 879 | Probe N°2
83 | 624 | VAV N°1 | 83 | 624 | VAV N°1 | 83 | 880 | Probe N°1
| 625 | VAV N°2 |  | 625 | VAV N°2 |  | 881 | Probe N°2
84 | 626 | VAV N°1 | 84 | 626 | VAV N°1 | 84 | 882 | Probe N°1
| 627 | VAV N°2 |  | 627 | VAV N°2 |  | 883 | Probe N°2
85 | 628 | VAV N°1 | 85 | 628 | VAV N°1 | 85 | 884 | Probe N°1
| 629 | VAV N°2 |  | 629 | VAV N°2 |  | 885 | Probe N°2
86 | 630 | VAV N°1 | 86 | 630 | VAV N°1 | 86 | 886 | Probe N°1
| 631 | VAV N°2 |  | 631 | VAV N°2 |  | 887 | Probe N°2
87 | 632 | VAV N°1 | 87 | 632 | VAV N°1 | 87 | 888 | Probe N°1
| 633 | VAV N°2 |  | 633 | VAV N°2 |  | 889 | Probe N°2
88 | 634 | VAV N°1 | 88 | 634 | VAV N°1 | 88 | 890 | Probe N°1
| 635 | VAV N°2 |  | 635 | VAV N°2 |  | 891 | Probe N°2
89 | 636 | VAV N°1 | 89 | 636 | VAV N°1 | 89 | 892 | Probe N°1
| 637 | VAV N°2 |  | 637 | VAV N°2 |  | 893 | Probe N°2
90 | 638 | VAV N°1 | 90 | 638 | VAV N°1 | 90 | 894 | Probe N°1
| 639 | VAV N°2 |  | 639 | VAV N°2 |  | 895 | Probe N°2
91 | 640 | VAV N°1 | 91 | 640 | VAV N°1 | 91 | 896 | Probe N°1
| 641 | VAV N°2 |  | 641 | VAV N°2 |  | 897 | Probe N°2
92 | 642 | VAV N°1 | 92 | 642 | VAV N°1 | 92 | 898 | Probe N°1
| 643 | VAV N°2 |  | 643 | VAV N°2 |  | 899 | Probe N°2
93 | 644 | VAV N°1 | 93 | 644 | VAV N°1 | 93 | 900 | Probe N°1
| 645 | VAV N°2 |  | 645 | VAV N°2 |  | 901 | Probe N°2
94 | 646 | VAV N°1 | 94 | 646 | VAV N°1 | 94 | 902 | Probe N°1
| 647 | VAV N°2 |  | 647 | VAV N°2 |  | 903 | Probe N°2
95 | 648 | VAV N°1 | 95 | 648 | VAV N°1 | 95 | 904 | Probe N°1
| 649 | VAV N°2 |  | 649 | VAV N°2 |  | 905 | Probe N°2
96 | 650 | VAV N°1 | 96 | 650 | VAV N°1 | 96 | 906 | Probe N°1
| 651 | VAV N°2 |  | 651 | VAV N°2 |  | 907 | Probe N°2
97 | 652 | VAV N°1 | 97 | 652 | VAV N°1 | 97 | 908 | Probe N°1
| 653 | VAV N°2 |  | 653 | VAV N°2 |  | 909 | Probe N°2
98 | 654 | VAV N°1 | 98 | 654 | VAV N°1 | 98 | 910 | Probe N°1
| 655 | VAV N°2 |  | 655 | VAV N°2 |  | 911 | Probe N°2
99 | 656 | VAV N°1 | 99 | 656 | VAV N°1 | 99 | 912 | Probe N°1
| 657 | VAV N°2 |  | 657 | VAV N°2 |  | 913 | Probe N°2
100 | 658 | VAV N°1 | 100 | 658 | VAV N°1 | 100 | 914 | Probe N°1
| 659 | VAV N°2 |  | 659 | VAV N°2 |  | 915 | Probe N°2
101 | 660 | VAV N°1 | 101 | 660 | VAV N°1 | 101 | 916 | Probe N°1
| 661 | VAV N°2 |  | 661 | VAV N°2 |  | 917 | Probe N°2
102 | 662 | VAV N°1 | 102 | 662 | VAV N°1 | 102 | 918 | Probe N°1
| 663 | VAV N°2 |  | 663 | VAV N°2 |  | 919 | Probe N°2
103 | 664 | VAV N°1 | 103 | 664 | VAV N°1 | 103 | 920 | Probe N°1
| 665 | VAV N°2 |  | 665 | VAV N°2 |  | 921 | Probe N°2
104 | 666 | VAV N°1 | 104 | 666 | VAV N°1 | 104 | 922 | Probe N°1
| 667 | VAV N°2 |  | 667 | VAV N°2 |  | 923 | Probe N°2
105 | 668 | VAV N°1 | 105 | 668 | VAV N°1 | 105 | 924 | Probe N°1
| 669 | VAV N°2 |  | 669 | VAV N°2 |  | 925 | Probe N°2
106 | 670 | VAV N°1 | 106 | 670 | VAV N°1 | 106 | 926 | Probe N°1
| 671 | VAV N°2 |  | 671 | VAV N°2 |  | 927 | Probe N°2
107 | 672 | VAV N°1 | 107 | 672 | VAV N°1 | 107 | 928 | Probe N°1
| 673 | VAV N°2 |  | 673 | VAV N°2 |  | 929 | Probe N°2
108 | 674 | VAV N°1 | 108 | 674 | VAV N°1 | 108 | 930 | Probe N°1
| 675 | VAV N°2 |  | 675 | VAV N°2 |  | 931 | Probe N°2
109 | 676 | VAV N°1 | 109 | 676 | VAV N°1 | 109 | 932 | Probe N°1
| 677 | VAV N°2 |  | 677 | VAV N°2 |  | 933 | Probe N°2
110 | 678 | VAV N°1 | 110 | 678 | VAV N°1 | 110 | 934 | Probe N°1
| 679 | VAV N°2 |  | 679 | VAV N°2 |  | 935 | Probe N°2
111 | 680 | VAV N°1 | 111 | 680 | VAV N°1 | 111 | 936 | Probe N°1
| 681 | VAV N°2 |  | 681 | VAV N°2 |  | 937 | Probe N°2
112 | 682 | VAV N°1 | 112 | 682 | VAV N°1 | 112 | 938 | Probe N°1
| 683 | VAV N°2 |  | 683 | VAV N°2 |  | 939 | Probe N°2
113 | 684 | VAV N°1 | 113 | 684 | VAV N°1 | 113 | 940 | Probe N°1
| 685 | VAV N°2 |  | 685 | VAV N°2 |  | 941 | Probe N°2
114 | 686 | VAV N°1 | 114 | 686 | VAV N°1 | 114 | 942 | Probe N°1
| 687 | VAV N°2 |  | 687 | VAV N°2 |  | 943 | Probe N°2
115 | 688 | VAV N°1 | 115 | 688 | VAV N°1 | 115 | 944 | Probe N°1
| 689 | VAV N°2 |  | 689 | VAV N°2 |  | 945 | Probe N°2
116 | 690 | VAV N°1 | 116 | 690 | VAV N°1 | 116 | 946 | Probe N°1
| 691 | VAV N°2 |  | 691 | VAV N°2 |  | 947 | Probe N°2
117 | 692 | VAV N°1 | 117 | 692 | VAV N°1 | 117 | 948 | Probe N°1
| 693 | VAV N°2 |  | 693 | VAV N°2 |  | 949 | Probe N°2
118 | 694 | VAV N°1 | 118 | 694 | VAV N°1 | 118 | 950 | Probe N°1
| 695 | VAV N°2 |  | 695 | VAV N°2 |  | 951 | Probe N°2
119 | 696 | VAV N°1 | 119 | 696 | VAV N°1 | 119 | 952 | Probe N°1
| 697 | VAV N°2 |  | 697 | VAV N°2 |  | 953 | Probe N°2
120 | 698 | VAV N°1 | 120 | 698 | VAV N°1 | 120 | 954 | Probe N°1
| 699 | VAV N°2 |  | 699 | VAV N°2 |  | 955 | Probe N°2
121 | 700 | VAV N°1 | 121 | 700 | VAV N°1 | 121 | 956 | Probe N°1
| 701 | VAV N°2 |  | 701 | VAV N°2 |  | 957 | Probe N°2
122 | 702 | VAV N°1 | 122 | 702 | VAV N°1 | 122 | 958 | Probe N°1
| 703 | VAV N°2 |  | 703 | VAV N°2 |  | 959 | Probe N°2
123 | 704 | VAV N°1 | 123 | 704 | VAV N°1 | 123 | 960 | Probe N°1
| 705 | VAV N°2 |  | 705 | VAV N°2 |  | 961 | Probe N°2
124 | 706 | VAV N°1 | 124 | 706 | VAV N°1 | 124 | 962 | Probe N°1
| 707 | VAV N°2 |  | 707 | VAV N°2 |  | 963 | Probe N°2
125 | 708 | VAV N°1 | 125 | 708 | VAV N°1 | 125 | 964 | Probe N°1
| 709 | VAV N°2 |  | 709 | VAV N°2 |  | 965 | Probe N°2
126 | 710 | VAV N°1 | 126 | 710 | VAV N°1 | 126 | 966 | Probe N°1
| 711 | VAV N°2 |  | 711 | VAV N°2 |  | 967 | Probe N°2
127 | 712 | VAV N°1 | 127 | 712 | VAV N°1 | 127 | 968 | Probe N°1
| 713 | VAV N°2 |  | 713 | VAV N°2 |  | 969 | Probe N°2
128 | 714 | VAV N°1 | 128 | 714 | VAV N°1 | 128 | 970 | Probe N°1
| 715 | VAV N°2 |  | 715 | VAV N°2 |  | 971 | Probe N°2

## EASY-R Smoke detector
Easy - R Smoke detector | [12 empty] | F2 = Failure detector 2
A2 = Alarm detector 2
F1 = Failure detector 1
A1 = Alarm detector 1
R2 = Reset Alarm 2
Easybus | modbus RTU |  |  |  |  | Easybus | modbus RTU |  |  | Easybus | modbus RTU |  | R1 = Reset Alarm 1
Address |  | Read (bits) |  |  |  | Address |  | Write (bits) |  | Address |  | Read (bits)
|  | F2 | A2 | F1 | A1 |  |  | R2 | R1 |  |  | Module error communication
1 | 332 | 3 | 2 | 1 | 0 | 1 | 308 | 1 | 0 | 1 | 300 | 0
2 |  | 7 | 6 | 5 | 4 | 2 |  | 3 | 2 | 2 |  | 4
3 |  | 11 | 10 | 9 | 8 | 3 |  | 5 | 4 | 3 |  | 8
4 |  | 15 | 14 | 13 | 12 | 4 |  | 7 | 6 | 4 |  | 12
5 | 333 | 3 | 2 | 1 | 0 | 5 |  | 9 | 8 | 5 | 301 | 0
6 |  | 7 | 6 | 5 | 4 | 6 |  | 11 | 10 | 6 |  | 4
7 |  | 11 | 10 | 9 | 8 | 7 |  | 13 | 12 | 7 |  | 8
8 |  | 15 | 14 | 13 | 12 | 8 |  | 15 | 14 | 8 |  | 12
9 | 334 | 3 | 2 | 1 | 0 | 9 | 309 | 1 | 0 | 9 | 302 | 0
10 |  | 7 | 6 | 5 | 4 | 10 |  | 3 | 2 | 10 |  | 4
11 |  | 11 | 10 | 9 | 8 | 11 |  | 5 | 4 | 11 |  | 8
12 |  | 15 | 14 | 13 | 12 | 12 |  | 7 | 6 | 12 |  | 12
13 | 335 | 3 | 2 | 1 | 0 | 13 |  | 9 | 8 | 13 | 303 | 0
14 |  | 7 | 6 | 5 | 4 | 14 |  | 11 | 10 | 14 |  | 4
15 |  | 11 | 10 | 9 | 8 | 15 |  | 13 | 12 | 15 |  | 8
16 |  | 15 | 14 | 13 | 12 | 16 |  | 15 | 14 | 16 |  | 12
17 | 336 | 3 | 2 | 1 | 0 | 17 | 310 | 1 | 0 | 17 | 304 | 0
18 |  | 7 | 6 | 5 | 4 | 18 |  | 3 | 2 | 18 |  | 4
19 |  | 11 | 10 | 9 | 8 | 19 |  | 5 | 4 | 19 |  | 8
20 |  | 15 | 14 | 13 | 12 | 20 |  | 7 | 6 | 20 |  | 12
21 | 337 | 3 | 2 | 1 | 0 | 21 |  | 9 | 8 | 21 | 305 | 0
22 |  | 7 | 6 | 5 | 4 | 22 |  | 11 | 10 | 22 |  | 4
23 |  | 11 | 10 | 9 | 8 | 23 |  | 13 | 12 | 23 |  | 8
24 |  | 15 | 14 | 13 | 12 | 24 |  | 15 | 14 | 24 |  | 12
25 | 338 | 3 | 2 | 1 | 0 | 25 | 311 | 1 | 0 | 25 | 306 | 0
26 |  | 7 | 6 | 5 | 4 | 26 |  | 3 | 2 | 26 |  | 4
27 |  | 11 | 10 | 9 | 8 | 27 |  | 5 | 4 | 27 |  | 8
28 |  | 15 | 14 | 13 | 12 | 28 |  | 7 | 6 | 28 |  | 12
29 | 339 | 3 | 2 | 1 | 0 | 29 |  | 9 | 8 | 29 | 307 | 0
30 |  | 7 | 6 | 5 | 4 | 30 |  | 11 | 10 | 30 |  | 4
31 |  | 11 | 10 | 9 | 8 | 31 |  | 13 | 12 | 31 |  | 8
32 |  | 15 | 14 | 13 | 12 | 32 |  | 15 | 14 | 32 |  | 12
33 | 340 | 3 | 2 | 1 | 0 | 33 | 312 | 1 | 0 | 33 | 308 | 0
34 |  | 7 | 6 | 5 | 4 | 34 |  | 3 | 2 | 34 |  | 4
35 |  | 11 | 10 | 9 | 8 | 35 |  | 5 | 4 | 35 |  | 8
36 |  | 15 | 14 | 13 | 12 | 36 |  | 7 | 6 | 36 |  | 12
37 | 341 | 3 | 2 | 1 | 0 | 37 |  | 9 | 8 | 37 | 309 | 0
38 |  | 7 | 6 | 5 | 4 | 38 |  | 11 | 10 | 38 |  | 4
39 |  | 11 | 10 | 9 | 8 | 39 |  | 13 | 12 | 39 |  | 8
40 |  | 15 | 14 | 13 | 12 | 40 |  | 15 | 14 | 40 |  | 12
41 | 342 | 3 | 2 | 1 | 0 | 41 | 313 | 1 | 0 | 41 | 310 | 0
42 |  | 7 | 6 | 5 | 4 | 42 |  | 3 | 2 | 42 |  | 4
43 |  | 11 | 10 | 9 | 8 | 43 |  | 5 | 4 | 43 |  | 8
44 |  | 15 | 14 | 13 | 12 | 44 |  | 7 | 6 | 44 |  | 12
45 | 343 | 3 | 2 | 1 | 0 | 45 |  | 9 | 8 | 45 | 311 | 0
46 |  | 7 | 6 | 5 | 4 | 46 |  | 11 | 10 | 46 |  | 4
47 |  | 11 | 10 | 9 | 8 | 47 |  | 13 | 12 | 47 |  | 8
48 |  | 15 | 14 | 13 | 12 | 48 |  | 15 | 14 | 48 |  | 12
49 | 344 | 3 | 2 | 1 | 0 | 49 | 314 | 1 | 0 | 49 | 312 | 0
50 |  | 7 | 6 | 5 | 4 | 50 |  | 3 | 2 | 50 |  | 4
51 |  | 11 | 10 | 9 | 8 | 51 |  | 5 | 4 | 51 |  | 8
52 |  | 15 | 14 | 13 | 12 | 52 |  | 7 | 6 | 52 |  | 12
53 | 345 | 3 | 2 | 1 | 0 | 53 |  | 9 | 8 | 53 | 313 | 0
54 |  | 7 | 6 | 5 | 4 | 54 |  | 11 | 10 | 54 |  | 4
55 |  | 11 | 10 | 9 | 8 | 55 |  | 13 | 12 | 55 |  | 8
56 |  | 15 | 14 | 13 | 12 | 56 |  | 15 | 14 | 56 |  | 12
57 | 346 | 3 | 2 | 1 | 0 | 57 | 315 | 1 | 0 | 57 | 314 | 0
58 |  | 7 | 6 | 5 | 4 | 58 |  | 3 | 2 | 58 |  | 4
59 |  | 11 | 10 | 9 | 8 | 59 |  | 5 | 4 | 59 |  | 8
60 |  | 15 | 14 | 13 | 12 | 60 |  | 7 | 6 | 60 |  | 12
61 | 347 | 3 | 2 | 1 | 0 | 61 |  | 9 | 8 | 61 | 315 | 0
62 |  | 7 | 6 | 5 | 4 | 62 |  | 11 | 10 | 62 |  | 4
63 |  | 11 | 10 | 9 | 8 | 63 |  | 13 | 12 | 63 |  | 8
64 |  | 15 | 14 | 13 | 12 | 64 |  | 15 | 14 | 64 |  | 12
65 | 348 | 3 | 2 | 1 | 0 | 65 | 316 | 1 | 0 | 65 | 316 | 0
66 |  | 7 | 6 | 5 | 4 | 66 |  | 3 | 2 | 66 |  | 4
67 |  | 11 | 10 | 9 | 8 | 67 |  | 5 | 4 | 67 |  | 8
68 |  | 15 | 14 | 13 | 12 | 68 |  | 7 | 6 | 68 |  | 12
69 | 349 | 3 | 2 | 1 | 0 | 69 |  | 9 | 8 | 69 | 317 | 0
70 |  | 7 | 6 | 5 | 4 | 70 |  | 11 | 10 | 70 |  | 4
71 |  | 11 | 10 | 9 | 8 | 71 |  | 13 | 12 | 71 |  | 8
72 |  | 15 | 14 | 13 | 12 | 72 |  | 15 | 14 | 72 |  | 12
73 | 350 | 3 | 2 | 1 | 0 | 73 | 317 | 1 | 0 | 73 | 318 | 0
74 |  | 7 | 6 | 5 | 4 | 74 |  | 3 | 2 | 74 |  | 4
75 |  | 11 | 10 | 9 | 8 | 75 |  | 5 | 4 | 75 |  | 8
76 |  | 15 | 14 | 13 | 12 | 76 |  | 7 | 6 | 76 |  | 12
77 | 351 | 3 | 2 | 1 | 0 | 77 |  | 9 | 8 | 77 | 319 | 0
78 |  | 7 | 6 | 5 | 4 | 78 |  | 11 | 10 | 78 |  | 4
79 |  | 11 | 10 | 9 | 8 | 79 |  | 13 | 12 | 79 |  | 8
80 |  | 15 | 14 | 13 | 12 | 80 |  | 15 | 14 | 80 |  | 12
81 | 352 | 3 | 2 | 1 | 0 | 81 | 318 | 1 | 0 | 81 | 320 | 0
82 |  | 7 | 6 | 5 | 4 | 82 |  | 3 | 2 | 82 |  | 4
83 |  | 11 | 10 | 9 | 8 | 83 |  | 5 | 4 | 83 |  | 8
84 |  | 15 | 14 | 13 | 12 | 84 |  | 7 | 6 | 84 |  | 12
85 | 353 | 3 | 2 | 1 | 0 | 85 |  | 9 | 8 | 85 | 321 | 0
86 |  | 7 | 6 | 5 | 4 | 86 |  | 11 | 10 | 86 |  | 4
87 |  | 11 | 10 | 9 | 8 | 87 |  | 13 | 12 | 87 |  | 8
88 |  | 15 | 14 | 13 | 12 | 88 |  | 15 | 14 | 88 |  | 12
89 | 354 | 3 | 2 | 1 | 0 | 89 | 319 | 1 | 0 | 89 | 322 | 0
90 |  | 7 | 6 | 5 | 4 | 90 |  | 3 | 2 | 90 |  | 4
91 |  | 11 | 10 | 9 | 8 | 91 |  | 5 | 4 | 91 |  | 8
92 |  | 15 | 14 | 13 | 12 | 92 |  | 7 | 6 | 92 |  | 12
93 | 355 | 3 | 2 | 1 | 0 | 93 |  | 9 | 8 | 93 | 323 | 0
94 |  | 7 | 6 | 5 | 4 | 94 |  | 11 | 10 | 94 |  | 4
95 |  | 11 | 10 | 9 | 8 | 95 |  | 13 | 12 | 95 |  | 8
96 |  | 15 | 14 | 13 | 12 | 96 |  | 15 | 14 | 96 |  | 12
97 | 356 | 3 | 2 | 1 | 0 | 97 | 320 | 1 | 0 | 97 | 324 | 0
98 |  | 7 | 6 | 5 | 4 | 98 |  | 3 | 2 | 98 |  | 4
99 |  | 11 | 10 | 9 | 8 | 99 |  | 5 | 4 | 99 |  | 8
100 |  | 15 | 14 | 13 | 12 | 100 |  | 7 | 6 | 100 |  | 12
101 | 357 | 3 | 2 | 1 | 0 | 101 |  | 9 | 8 | 101 | 325 | 0
102 |  | 7 | 6 | 5 | 4 | 102 |  | 11 | 10 | 102 |  | 4
103 |  | 11 | 10 | 9 | 8 | 103 |  | 13 | 12 | 103 |  | 8
104 |  | 15 | 14 | 13 | 12 | 104 |  | 15 | 14 | 104 |  | 12
105 | 358 | 3 | 2 | 1 | 0 | 105 | 321 | 1 | 0 | 105 | 326 | 0
106 |  | 7 | 6 | 5 | 4 | 106 |  | 3 | 2 | 106 |  | 4
107 |  | 11 | 10 | 9 | 8 | 107 |  | 5 | 4 | 107 |  | 8
108 |  | 15 | 14 | 13 | 12 | 108 |  | 7 | 6 | 108 |  | 12
109 | 359 | 3 | 2 | 1 | 0 | 109 |  | 9 | 8 | 109 | 327 | 0
110 |  | 7 | 6 | 5 | 4 | 110 |  | 11 | 10 | 110 |  | 4
111 |  | 11 | 10 | 9 | 8 | 111 |  | 13 | 12 | 111 |  | 8
112 |  | 15 | 14 | 13 | 12 | 112 |  | 15 | 14 | 112 |  | 12
113 | 360 | 3 | 2 | 1 | 0 | 113 | 322 | 1 | 0 | 113 | 328 | 0
114 |  | 7 | 6 | 5 | 4 | 114 |  | 3 | 2 | 114 |  | 4
115 |  | 11 | 10 | 9 | 8 | 115 |  | 5 | 4 | 115 |  | 8
116 |  | 15 | 14 | 13 | 12 | 116 |  | 7 | 6 | 116 |  | 12
117 | 361 | 3 | 2 | 1 | 0 | 117 |  | 9 | 8 | 117 | 329 | 0
118 |  | 7 | 6 | 5 | 4 | 118 |  | 11 | 10 | 118 |  | 4
119 |  | 11 | 10 | 9 | 8 | 119 |  | 13 | 12 | 119 |  | 8
120 |  | 15 | 14 | 13 | 12 | 120 |  | 15 | 14 | 120 |  | 12
121 | 362 | 3 | 2 | 1 | 0 | 121 | 323 | 1 | 0 | 121 | 330 | 0
122 |  | 7 | 6 | 5 | 4 | 122 |  | 3 | 2 | 122 |  | 4
123 |  | 11 | 10 | 9 | 8 | 123 |  | 5 | 4 | 123 |  | 8
124 |  | 15 | 14 | 13 | 12 | 124 |  | 7 | 6 | 124 |  | 12
125 | 363 | 3 | 2 | 1 | 0 | 125 |  | 9 | 8 | 125 | 331 | 0
126 |  | 7 | 6 | 5 | 4 | 126 |  | 11 | 10 | 126 |  | 4
127 |  | 11 | 10 | 9 | 8 | 127 |  | 13 | 12 | 127 |  | 8
128 |  | 15 | 14 | 13 | 12 | 128 |  | 15 | 14 | 128 |  | 12

## EASY-CO2
Easy-CO2
Easybus | modbus RTU |  | Easybus | modbus RTU |  | Easybus | modbus RTU | Easybus | modbus RTU |  | Easybus | modbus RTU
Address |  | Read VAV | Address |  | Write PID | Address write setpoint |  | Address |  | Read sensor | Address |  | Read (bits)
|  | 0-1000 |  |  | 0-1000 |  |  |  |  | 0-1000 |  |  | Module error communication
1 | 460 | VAV N°1 | 1 | 460 | Factor Kp | 1 | 716 | 1 | 716 | Probe N°1 | 1 | 300 | 0
| 461 | VAV N°2 |  | 461 | Factor Ki |  |  |  | 717 | Probe N°2 | 2 |  | 4
2 | 462 | VAV N°1 | 2 | 462 | Factor Kp | 2 | 717 | 2 | 718 | Probe N°1 | 3 |  | 8
| 463 | VAV N°2 |  | 463 | Factor Ki |  |  |  | 719 | Probe N°2 | 4 |  | 12
3 | 464 | VAV N°1 | 3 | 464 | Factor Kp | 3 | 718 | 3 | 720 | Probe N°1 | 5 | 301 | 0
| 465 | VAV N°2 |  | 465 | Factor Ki |  |  |  | 721 | Probe N°2 | 6 |  | 4
4 | 466 | VAV N°1 | 4 | 466 | Factor Kp | 4 | 719 | 4 | 722 | Probe N°1 | 7 |  | 8
| 467 | VAV N°2 |  | 467 | Factor Ki |  |  |  | 723 | Probe N°2 | 8 |  | 12
5 | 468 | VAV N°1 | 5 | 468 | Factor Kp | 5 | 720 | 5 | 724 | Probe N°1 | 9 | 302 | 0
| 469 | VAV N°2 |  | 469 | Factor Ki |  |  |  | 725 | Probe N°2 | 10 |  | 4
6 | 470 | VAV N°1 | 6 | 470 | Factor Kp | 6 | 721 | 6 | 726 | Probe N°1 | 11 |  | 8
| 471 | VAV N°2 |  | 471 | Factor Ki |  |  |  | 727 | Probe N°2 | 12 |  | 12
7 | 472 | VAV N°1 | 7 | 472 | Factor Kp | 7 | 722 | 7 | 728 | Probe N°1 | 13 | 303 | 0
| 473 | VAV N°2 |  | 473 | Factor Ki |  |  |  | 729 | Probe N°2 | 14 |  | 4
8 | 474 | VAV N°1 | 8 | 474 | Factor Kp | 8 | 723 | 8 | 730 | Probe N°1 | 15 |  | 8
| 475 | VAV N°2 |  | 475 | Factor Ki |  |  |  | 731 | Probe N°2 | 16 |  | 12
9 | 476 | VAV N°1 | 9 | 476 | Factor Kp | 9 | 724 | 9 | 732 | Probe N°1 | 17 | 304 | 0
| 477 | VAV N°2 |  | 477 | Factor Ki |  |  |  | 733 | Probe N°2 | 18 |  | 4
10 | 478 | VAV N°1 | 10 | 478 | Factor Kp | 10 | 725 | 10 | 734 | Probe N°1 | 19 |  | 8
| 479 | VAV N°2 |  | 479 | Factor Ki |  |  |  | 735 | Probe N°2 | 20 |  | 12
11 | 480 | VAV N°1 | 11 | 480 | Factor Kp | 11 | 726 | 11 | 736 | Probe N°1 | 21 | 305 | 0
| 481 | VAV N°2 |  | 481 | Factor Ki |  |  |  | 737 | Probe N°2 | 22 |  | 4
12 | 482 | VAV N°1 | 12 | 482 | Factor Kp | 12 | 727 | 12 | 738 | Probe N°1 | 23 |  | 8
| 483 | VAV N°2 |  | 483 | Factor Ki |  |  |  | 739 | Probe N°2 | 24 |  | 12
13 | 484 | VAV N°1 | 13 | 484 | Factor Kp | 13 | 728 | 13 | 740 | Probe N°1 | 25 | 306 | 0
| 485 | VAV N°2 |  | 485 | Factor Ki |  |  |  | 741 | Probe N°2 | 26 |  | 4
14 | 486 | VAV N°1 | 14 | 486 | Factor Kp | 14 | 729 | 14 | 742 | Probe N°1 | 27 |  | 8
| 487 | VAV N°2 |  | 487 | Factor Ki |  |  |  | 743 | Probe N°2 | 28 |  | 12
15 | 488 | VAV N°1 | 15 | 488 | Factor Kp | 15 | 730 | 15 | 744 | Probe N°1 | 29 | 307 | 0
| 489 | VAV N°2 |  | 489 | Factor Ki |  |  |  | 745 | Probe N°2 | 30 |  | 4
16 | 490 | VAV N°1 | 16 | 490 | Factor Kp | 16 | 731 | 16 | 746 | Probe N°1 | 31 |  | 8
| 491 | VAV N°2 |  | 491 | Factor Ki |  |  |  | 747 | Probe N°2 | 32 |  | 12
17 | 492 | VAV N°1 | 17 | 492 | Factor Kp | 17 | 732 | 17 | 748 | Probe N°1 | 33 | 308 | 0
| 493 | VAV N°2 |  | 493 | Factor Ki |  |  |  | 749 | Probe N°2 | 34 |  | 4
18 | 494 | VAV N°1 | 18 | 494 | Factor Kp | 18 | 733 | 18 | 750 | Probe N°1 | 35 |  | 8
| 495 | VAV N°2 |  | 495 | Factor Ki |  |  |  | 751 | Probe N°2 | 36 |  | 12
19 | 496 | VAV N°1 | 19 | 496 | Factor Kp | 19 | 734 | 19 | 752 | Probe N°1 | 37 | 309 | 0
| 497 | VAV N°2 |  | 497 | Factor Ki |  |  |  | 753 | Probe N°2 | 38 |  | 4
20 | 498 | VAV N°1 | 20 | 498 | Factor Kp | 20 | 735 | 20 | 754 | Probe N°1 | 39 |  | 8
| 499 | VAV N°2 |  | 499 | Factor Ki |  |  |  | 755 | Probe N°2 | 40 |  | 12
21 | 500 | VAV N°1 | 21 | 500 | Factor Kp | 21 | 736 | 21 | 756 | Probe N°1 | 41 | 310 | 0
| 501 | VAV N°2 |  | 501 | Factor Ki |  |  |  | 757 | Probe N°2 | 42 |  | 4
22 | 502 | VAV N°1 | 22 | 502 | Factor Kp | 22 | 737 | 22 | 758 | Probe N°1 | 43 |  | 8
| 503 | VAV N°2 |  | 503 | Factor Ki |  |  |  | 759 | Probe N°2 | 44 |  | 12
23 | 504 | VAV N°1 | 23 | 504 | Factor Kp | 23 | 738 | 23 | 760 | Probe N°1 | 45 | 311 | 0
| 505 | VAV N°2 |  | 505 | Factor Ki |  |  |  | 761 | Probe N°2 | 46 |  | 4
24 | 506 | VAV N°1 | 24 | 506 | Factor Kp | 24 | 739 | 24 | 762 | Probe N°1 | 47 |  | 8
| 507 | VAV N°2 |  | 507 | Factor Ki |  |  |  | 763 | Probe N°2 | 48 |  | 12
25 | 508 | VAV N°1 | 25 | 508 | Factor Kp | 25 | 740 | 25 | 764 | Probe N°1 | 49 | 312 | 0
| 509 | VAV N°2 |  | 509 | Factor Ki |  |  |  | 765 | Probe N°2 | 50 |  | 4
26 | 510 | VAV N°1 | 26 | 510 | Factor Kp | 26 | 741 | 26 | 766 | Probe N°1 | 51 |  | 8
| 511 | VAV N°2 |  | 511 | Factor Ki |  |  |  | 767 | Probe N°2 | 52 |  | 12
27 | 512 | VAV N°1 | 27 | 512 | Factor Kp | 27 | 742 | 27 | 768 | Probe N°1 | 53 | 313 | 0
| 513 | VAV N°2 |  | 513 | Factor Ki |  |  |  | 769 | Probe N°2 | 54 |  | 4
28 | 514 | VAV N°1 | 28 | 514 | Factor Kp | 28 | 743 | 28 | 770 | Probe N°1 | 55 |  | 8
| 515 | VAV N°2 |  | 515 | Factor Ki |  |  |  | 771 | Probe N°2 | 56 |  | 12
29 | 516 | VAV N°1 | 29 | 516 | Factor Kp | 29 | 744 | 29 | 772 | Probe N°1 | 57 | 314 | 0
| 517 | VAV N°2 |  | 517 | Factor Ki |  |  |  | 773 | Probe N°2 | 58 |  | 4
30 | 518 | VAV N°1 | 30 | 518 | Factor Kp | 30 | 745 | 30 | 774 | Probe N°1 | 59 |  | 8
| 519 | VAV N°2 |  | 519 | Factor Ki |  |  |  | 775 | Probe N°2 | 60 |  | 12
31 | 520 | VAV N°1 | 31 | 520 | Factor Kp | 31 | 746 | 31 | 776 | Probe N°1 | 61 | 315 | 0
| 521 | VAV N°2 |  | 521 | Factor Ki |  |  |  | 777 | Probe N°2 | 62 |  | 4
32 | 522 | VAV N°1 | 32 | 522 | Factor Kp | 32 | 747 | 32 | 778 | Probe N°1 | 63 |  | 8
| 523 | VAV N°2 |  | 523 | Factor Ki |  |  |  | 779 | Probe N°2 | 64 |  | 12
33 | 524 | VAV N°1 | 33 | 524 | Factor Kp | 33 | 748 | 33 | 780 | Probe N°1 | 65 | 316 | 0
| 525 | VAV N°2 |  | 525 | Factor Ki |  |  |  | 781 | Probe N°2 | 66 |  | 4
34 | 526 | VAV N°1 | 34 | 526 | Factor Kp | 34 | 749 | 34 | 782 | Probe N°1 | 67 |  | 8
| 527 | VAV N°2 |  | 527 | Factor Ki |  |  |  | 783 | Probe N°2 | 68 |  | 12
35 | 528 | VAV N°1 | 35 | 528 | Factor Kp | 35 | 750 | 35 | 784 | Probe N°1 | 69 | 317 | 0
| 529 | VAV N°2 |  | 529 | Factor Ki |  |  |  | 785 | Probe N°2 | 70 |  | 4
36 | 530 | VAV N°1 | 36 | 530 | Factor Kp | 36 | 751 | 36 | 786 | Probe N°1 | 71 |  | 8
| 531 | VAV N°2 |  | 531 | Factor Ki |  |  |  | 787 | Probe N°2 | 72 |  | 12
37 | 532 | VAV N°1 | 37 | 532 | Factor Kp | 37 | 752 | 37 | 788 | Probe N°1 | 73 | 318 | 0
| 533 | VAV N°2 |  | 533 | Factor Ki |  |  |  | 789 | Probe N°2 | 74 |  | 4
38 | 534 | VAV N°1 | 38 | 534 | Factor Kp | 38 | 753 | 38 | 790 | Probe N°1 | 75 |  | 8
| 535 | VAV N°2 |  | 535 | Factor Ki |  |  |  | 791 | Probe N°2 | 76 |  | 12
39 | 536 | VAV N°1 | 39 | 536 | Factor Kp | 39 | 754 | 39 | 792 | Probe N°1 | 77 | 319 | 0
| 537 | VAV N°2 |  | 537 | Factor Ki |  |  |  | 793 | Probe N°2 | 78 |  | 4
40 | 538 | VAV N°1 | 40 | 538 | Factor Kp | 40 | 755 | 40 | 794 | Probe N°1 | 79 |  | 8
| 539 | VAV N°2 |  | 539 | Factor Ki |  |  |  | 795 | Probe N°2 | 80 |  | 12
41 | 540 | VAV N°1 | 41 | 540 | Factor Kp | 41 | 756 | 41 | 796 | Probe N°1 | 81 | 320 | 0
| 541 | VAV N°2 |  | 541 | Factor Ki |  |  |  | 797 | Probe N°2 | 82 |  | 4
42 | 542 | VAV N°1 | 42 | 542 | Factor Kp | 42 | 757 | 42 | 798 | Probe N°1 | 83 |  | 8
| 543 | VAV N°2 |  | 543 | Factor Ki |  |  |  | 799 | Probe N°2 | 84 |  | 12
43 | 544 | VAV N°1 | 43 | 544 | Factor Kp | 43 | 758 | 43 | 800 | Probe N°1 | 85 | 321 | 0
| 545 | VAV N°2 |  | 545 | Factor Ki |  |  |  | 801 | Probe N°2 | 86 |  | 4
44 | 546 | VAV N°1 | 44 | 546 | Factor Kp | 44 | 759 | 44 | 802 | Probe N°1 | 87 |  | 8
| 547 | VAV N°2 |  | 547 | Factor Ki |  |  |  | 803 | Probe N°2 | 88 |  | 12
45 | 548 | VAV N°1 | 45 | 548 | Factor Kp | 45 | 760 | 45 | 804 | Probe N°1 | 89 | 322 | 0
| 549 | VAV N°2 |  | 549 | Factor Ki |  |  |  | 805 | Probe N°2 | 90 |  | 4
46 | 550 | VAV N°1 | 46 | 550 | Factor Kp | 46 | 761 | 46 | 806 | Probe N°1 | 91 |  | 8
| 551 | VAV N°2 |  | 551 | Factor Ki |  |  |  | 807 | Probe N°2 | 92 |  | 12
47 | 552 | VAV N°1 | 47 | 552 | Factor Kp | 47 | 762 | 47 | 808 | Probe N°1 | 93 | 323 | 0
| 553 | VAV N°2 |  | 553 | Factor Ki |  |  |  | 809 | Probe N°2 | 94 |  | 4
48 | 554 | VAV N°1 | 48 | 554 | Factor Kp | 48 | 763 | 48 | 810 | Probe N°1 | 95 |  | 8
| 555 | VAV N°2 |  | 555 | Factor Ki |  |  |  | 811 | Probe N°2 | 96 |  | 12
49 | 556 | VAV N°1 | 49 | 556 | Factor Kp | 49 | 764 | 49 | 812 | Probe N°1 | 97 | 324 | 0
| 557 | VAV N°2 |  | 557 | Factor Ki |  |  |  | 813 | Probe N°2 | 98 |  | 4
50 | 558 | VAV N°1 | 50 | 558 | Factor Kp | 50 | 765 | 50 | 814 | Probe N°1 | 99 |  | 8
| 559 | VAV N°2 |  | 559 | Factor Ki |  |  |  | 815 | Probe N°2 | 100 |  | 12
51 | 560 | VAV N°1 | 51 | 560 | Factor Kp | 51 | 766 | 51 | 816 | Probe N°1 | 101 | 325 | 0
| 561 | VAV N°2 |  | 561 | Factor Ki |  |  |  | 817 | Probe N°2 | 102 |  | 4
52 | 562 | VAV N°1 | 52 | 562 | Factor Kp | 52 | 767 | 52 | 818 | Probe N°1 | 103 |  | 8
| 563 | VAV N°2 |  | 563 | Factor Ki |  |  |  | 819 | Probe N°2 | 104 |  | 12
53 | 564 | VAV N°1 | 53 | 564 | Factor Kp | 53 | 768 | 53 | 820 | Probe N°1 | 105 | 326 | 0
| 565 | VAV N°2 |  | 565 | Factor Ki |  |  |  | 821 | Probe N°2 | 106 |  | 4
54 | 566 | VAV N°1 | 54 | 566 | Factor Kp | 54 | 769 | 54 | 822 | Probe N°1 | 107 |  | 8
| 567 | VAV N°2 |  | 567 | Factor Ki |  |  |  | 823 | Probe N°2 | 108 |  | 12
55 | 568 | VAV N°1 | 55 | 568 | Factor Kp | 55 | 770 | 55 | 824 | Probe N°1 | 109 | 327 | 0
| 569 | VAV N°2 |  | 569 | Factor Ki |  |  |  | 825 | Probe N°2 | 110 |  | 4
56 | 570 | VAV N°1 | 56 | 570 | Factor Kp | 56 | 771 | 56 | 826 | Probe N°1 | 111 |  | 8
| 571 | VAV N°2 |  | 571 | Factor Ki |  |  |  | 827 | Probe N°2 | 112 |  | 12
57 | 572 | VAV N°1 | 57 | 572 | Factor Kp | 57 | 772 | 57 | 828 | Probe N°1 | 113 | 328 | 0
| 573 | VAV N°2 |  | 573 | Factor Ki |  |  |  | 829 | Probe N°2 | 114 |  | 4
58 | 574 | VAV N°1 | 58 | 574 | Factor Kp | 58 | 773 | 58 | 830 | Probe N°1 | 115 |  | 8
| 575 | VAV N°2 |  | 575 | Factor Ki |  |  |  | 831 | Probe N°2 | 116 |  | 12
59 | 576 | VAV N°1 | 59 | 576 | Factor Kp | 59 | 774 | 59 | 832 | Probe N°1 | 117 | 329 | 0
| 577 | VAV N°2 |  | 577 | Factor Ki |  |  |  | 833 | Probe N°2 | 118 |  | 4
60 | 578 | VAV N°1 | 60 | 578 | Factor Kp | 60 | 775 | 60 | 834 | Probe N°1 | 119 |  | 8
| 579 | VAV N°2 |  | 579 | Factor Ki |  |  |  | 835 | Probe N°2 | 120 |  | 12
61 | 580 | VAV N°1 | 61 | 580 | Factor Kp | 61 | 776 | 61 | 836 | Probe N°1 | 121 | 330 | 0
| 581 | VAV N°2 |  | 581 | Factor Ki |  |  |  | 837 | Probe N°2 | 122 |  | 4
62 | 582 | VAV N°1 | 62 | 582 | Factor Kp | 62 | 777 | 62 | 838 | Probe N°1 | 123 |  | 8
| 583 | VAV N°2 |  | 583 | Factor Ki |  |  |  | 839 | Probe N°2 | 124 |  | 12
63 | 584 | VAV N°1 | 63 | 584 | Factor Kp | 63 | 778 | 63 | 840 | Probe N°1 | 125 | 331 | 0
| 585 | VAV N°2 |  | 585 | Factor Ki |  |  |  | 841 | Probe N°2 | 126 |  | 4
64 | 586 | VAV N°1 | 64 | 586 | Factor Kp | 64 | 779 | 64 | 842 | Probe N°1 | 127 |  | 8
| 587 | VAV N°2 |  | 587 | Factor Ki |  |  |  | 843 | Probe N°2 | 128 |  | 12
65 | 588 | VAV N°1 | 65 | 588 | Factor Kp | 65 | 780 | 65 | 844 | Probe N°1
| 589 | VAV N°2 |  | 589 | Factor Ki |  |  |  | 845 | Probe N°2
66 | 590 | VAV N°1 | 66 | 590 | Factor Kp | 66 | 781 | 66 | 846 | Probe N°1
| 591 | VAV N°2 |  | 591 | Factor Ki |  |  |  | 847 | Probe N°2
67 | 592 | VAV N°1 | 67 | 592 | Factor Kp | 67 | 782 | 67 | 848 | Probe N°1
| 593 | VAV N°2 |  | 593 | Factor Ki |  |  |  | 849 | Probe N°2
68 | 594 | VAV N°1 | 68 | 594 | Factor Kp | 68 | 783 | 68 | 850 | Probe N°1
| 595 | VAV N°2 |  | 595 | Factor Ki |  |  |  | 851 | Probe N°2
69 | 596 | VAV N°1 | 69 | 596 | Factor Kp | 69 | 784 | 69 | 852 | Probe N°1
| 597 | VAV N°2 |  | 597 | Factor Ki |  |  |  | 853 | Probe N°2
70 | 598 | VAV N°1 | 70 | 598 | Factor Kp | 70 | 785 | 70 | 854 | Probe N°1
| 599 | VAV N°2 |  | 599 | Factor Ki |  |  |  | 855 | Probe N°2
71 | 600 | VAV N°1 | 71 | 600 | Factor Kp | 71 | 786 | 71 | 856 | Probe N°1
| 601 | VAV N°2 |  | 601 | Factor Ki |  |  |  | 857 | Probe N°2
72 | 602 | VAV N°1 | 72 | 602 | Factor Kp | 72 | 787 | 72 | 858 | Probe N°1
| 603 | VAV N°2 |  | 603 | Factor Ki |  |  |  | 859 | Probe N°2
73 | 604 | VAV N°1 | 73 | 604 | Factor Kp | 73 | 788 | 73 | 860 | Probe N°1
| 605 | VAV N°2 |  | 605 | Factor Ki |  |  |  | 861 | Probe N°2
74 | 606 | VAV N°1 | 74 | 606 | Factor Kp | 74 | 789 | 74 | 862 | Probe N°1
| 607 | VAV N°2 |  | 607 | Factor Ki |  |  |  | 863 | Probe N°2
75 | 608 | VAV N°1 | 75 | 608 | Factor Kp | 75 | 790 | 75 | 864 | Probe N°1
| 609 | VAV N°2 |  | 609 | Factor Ki |  |  |  | 865 | Probe N°2
76 | 610 | VAV N°1 | 76 | 610 | Factor Kp | 76 | 791 | 76 | 866 | Probe N°1
| 611 | VAV N°2 |  | 611 | Factor Ki |  |  |  | 867 | Probe N°2
77 | 612 | VAV N°1 | 77 | 612 | Factor Kp | 77 | 792 | 77 | 868 | Probe N°1
| 613 | VAV N°2 |  | 613 | Factor Ki |  |  |  | 869 | Probe N°2
78 | 614 | VAV N°1 | 78 | 614 | Factor Kp | 78 | 793 | 78 | 870 | Probe N°1
| 615 | VAV N°2 |  | 615 | Factor Ki |  |  |  | 871 | Probe N°2
79 | 616 | VAV N°1 | 79 | 616 | Factor Kp | 79 | 794 | 79 | 872 | Probe N°1
| 617 | VAV N°2 |  | 617 | Factor Ki |  |  |  | 873 | Probe N°2
80 | 618 | VAV N°1 | 80 | 618 | Factor Kp | 80 | 795 | 80 | 874 | Probe N°1
| 619 | VAV N°2 |  | 619 | Factor Ki |  |  |  | 875 | Probe N°2
81 | 620 | VAV N°1 | 81 | 620 | Factor Kp | 81 | 796 | 81 | 876 | Probe N°1
| 621 | VAV N°2 |  | 621 | Factor Ki |  |  |  | 877 | Probe N°2
82 | 622 | VAV N°1 | 82 | 622 | Factor Kp | 82 | 797 | 82 | 878 | Probe N°1
| 623 | VAV N°2 |  | 623 | Factor Ki |  |  |  | 879 | Probe N°2
83 | 624 | VAV N°1 | 83 | 624 | Factor Kp | 83 | 798 | 83 | 880 | Probe N°1
| 625 | VAV N°2 |  | 625 | Factor Ki |  |  |  | 881 | Probe N°2
84 | 626 | VAV N°1 | 84 | 626 | Factor Kp | 84 | 799 | 84 | 882 | Probe N°1
| 627 | VAV N°2 |  | 627 | Factor Ki |  |  |  | 883 | Probe N°2
85 | 628 | VAV N°1 | 85 | 628 | Factor Kp | 85 | 800 | 85 | 884 | Probe N°1
| 629 | VAV N°2 |  | 629 | Factor Ki |  |  |  | 885 | Probe N°2
86 | 630 | VAV N°1 | 86 | 630 | Factor Kp | 86 | 801 | 86 | 886 | Probe N°1
| 631 | VAV N°2 |  | 631 | Factor Ki |  |  |  | 887 | Probe N°2
87 | 632 | VAV N°1 | 87 | 632 | Factor Kp | 87 | 802 | 87 | 888 | Probe N°1
| 633 | VAV N°2 |  | 633 | Factor Ki |  |  |  | 889 | Probe N°2
88 | 634 | VAV N°1 | 88 | 634 | Factor Kp | 88 | 803 | 88 | 890 | Probe N°1
| 635 | VAV N°2 |  | 635 | Factor Ki |  |  |  | 891 | Probe N°2
89 | 636 | VAV N°1 | 89 | 636 | Factor Kp | 89 | 804 | 89 | 892 | Probe N°1
| 637 | VAV N°2 |  | 637 | Factor Ki |  |  |  | 893 | Probe N°2
90 | 638 | VAV N°1 | 90 | 638 | Factor Kp | 90 | 805 | 90 | 894 | Probe N°1
| 639 | VAV N°2 |  | 639 | Factor Ki |  |  |  | 895 | Probe N°2
91 | 640 | VAV N°1 | 91 | 640 | Factor Kp | 91 | 806 | 91 | 896 | Probe N°1
| 641 | VAV N°2 |  | 641 | Factor Ki |  |  |  | 897 | Probe N°2
92 | 642 | VAV N°1 | 92 | 642 | Factor Kp | 92 | 807 | 92 | 898 | Probe N°1
| 643 | VAV N°2 |  | 643 | Factor Ki |  |  |  | 899 | Probe N°2
93 | 644 | VAV N°1 | 93 | 644 | Factor Kp | 93 | 808 | 93 | 900 | Probe N°1
| 645 | VAV N°2 |  | 645 | Factor Ki |  |  |  | 901 | Probe N°2
94 | 646 | VAV N°1 | 94 | 646 | Factor Kp | 94 | 809 | 94 | 902 | Probe N°1
| 647 | VAV N°2 |  | 647 | Factor Ki |  |  |  | 903 | Probe N°2
95 | 648 | VAV N°1 | 95 | 648 | Factor Kp | 95 | 810 | 95 | 904 | Probe N°1
| 649 | VAV N°2 |  | 649 | Factor Ki |  |  |  | 905 | Probe N°2
96 | 650 | VAV N°1 | 96 | 650 | Factor Kp | 96 | 811 | 96 | 906 | Probe N°1
| 651 | VAV N°2 |  | 651 | Factor Ki |  |  |  | 907 | Probe N°2
97 | 652 | VAV N°1 | 97 | 652 | Factor Kp | 97 | 812 | 97 | 908 | Probe N°1
| 653 | VAV N°2 |  | 653 | Factor Ki |  |  |  | 909 | Probe N°2
98 | 654 | VAV N°1 | 98 | 654 | Factor Kp | 98 | 813 | 98 | 910 | Probe N°1
| 655 | VAV N°2 |  | 655 | Factor Ki |  |  |  | 911 | Probe N°2
99 | 656 | VAV N°1 | 99 | 656 | Factor Kp | 99 | 814 | 99 | 912 | Probe N°1
| 657 | VAV N°2 |  | 657 | Factor Ki |  |  |  | 913 | Probe N°2
100 | 658 | VAV N°1 | 100 | 658 | Factor Kp | 100 | 815 | 100 | 914 | Probe N°1
| 659 | VAV N°2 |  | 659 | Factor Ki |  |  |  | 915 | Probe N°2
101 | 660 | VAV N°1 | 101 | 660 | Factor Kp | 101 | 816 | 101 | 916 | Probe N°1
| 661 | VAV N°2 |  | 661 | Factor Ki |  |  |  | 917 | Probe N°2
102 | 662 | VAV N°1 | 102 | 662 | Factor Kp | 102 | 817 | 102 | 918 | Probe N°1
| 663 | VAV N°2 |  | 663 | Factor Ki |  |  |  | 919 | Probe N°2
103 | 664 | VAV N°1 | 103 | 664 | Factor Kp | 103 | 818 | 103 | 920 | Probe N°1
| 665 | VAV N°2 |  | 665 | Factor Ki |  |  |  | 921 | Probe N°2
104 | 666 | VAV N°1 | 104 | 666 | Factor Kp | 104 | 819 | 104 | 922 | Probe N°1
| 667 | VAV N°2 |  | 667 | Factor Ki |  |  |  | 923 | Probe N°2
105 | 668 | VAV N°1 | 105 | 668 | Factor Kp | 105 | 820 | 105 | 924 | Probe N°1
| 669 | VAV N°2 |  | 669 | Factor Ki |  |  |  | 925 | Probe N°2
106 | 670 | VAV N°1 | 106 | 670 | Factor Kp | 106 | 821 | 106 | 926 | Probe N°1
| 671 | VAV N°2 |  | 671 | Factor Ki |  |  |  | 927 | Probe N°2
107 | 672 | VAV N°1 | 107 | 672 | Factor Kp | 107 | 822 | 107 | 928 | Probe N°1
| 673 | VAV N°2 |  | 673 | Factor Ki |  |  |  | 929 | Probe N°2
108 | 674 | VAV N°1 | 108 | 674 | Factor Kp | 108 | 823 | 108 | 930 | Probe N°1
| 675 | VAV N°2 |  | 675 | Factor Ki |  |  |  | 931 | Probe N°2
109 | 676 | VAV N°1 | 109 | 676 | Factor Kp | 109 | 824 | 109 | 932 | Probe N°1
| 677 | VAV N°2 |  | 677 | Factor Ki |  |  |  | 933 | Probe N°2
110 | 678 | VAV N°1 | 110 | 678 | Factor Kp | 110 | 825 | 110 | 934 | Probe N°1
| 679 | VAV N°2 |  | 679 | Factor Ki |  |  |  | 935 | Probe N°2
111 | 680 | VAV N°1 | 111 | 680 | Factor Kp | 111 | 826 | 111 | 936 | Probe N°1
| 681 | VAV N°2 |  | 681 | Factor Ki |  |  |  | 937 | Probe N°2
112 | 682 | VAV N°1 | 112 | 682 | Factor Kp | 112 | 827 | 112 | 938 | Probe N°1
| 683 | VAV N°2 |  | 683 | Factor Ki |  |  |  | 939 | Probe N°2
113 | 684 | VAV N°1 | 113 | 684 | Factor Kp | 113 | 828 | 113 | 940 | Probe N°1
| 685 | VAV N°2 |  | 685 | Factor Ki |  |  |  | 941 | Probe N°2
114 | 686 | VAV N°1 | 114 | 686 | Factor Kp | 114 | 829 | 114 | 942 | Probe N°1
| 687 | VAV N°2 |  | 687 | Factor Ki |  |  |  | 943 | Probe N°2
115 | 688 | VAV N°1 | 115 | 688 | Factor Kp | 115 | 830 | 115 | 944 | Probe N°1
| 689 | VAV N°2 |  | 689 | Factor Ki |  |  |  | 945 | Probe N°2
116 | 690 | VAV N°1 | 116 | 690 | Factor Kp | 116 | 831 | 116 | 946 | Probe N°1
| 691 | VAV N°2 |  | 691 | Factor Ki |  |  |  | 947 | Probe N°2
117 | 692 | VAV N°1 | 117 | 692 | Factor Kp | 117 | 832 | 117 | 948 | Probe N°1
| 693 | VAV N°2 |  | 693 | Factor Ki |  |  |  | 949 | Probe N°2
118 | 694 | VAV N°1 | 118 | 694 | Factor Kp | 118 | 833 | 118 | 950 | Probe N°1
| 695 | VAV N°2 |  | 695 | Factor Ki |  |  |  | 951 | Probe N°2
119 | 696 | VAV N°1 | 119 | 696 | Factor Kp | 119 | 834 | 119 | 952 | Probe N°1
| 697 | VAV N°2 |  | 697 | Factor Ki |  |  |  | 953 | Probe N°2
120 | 698 | VAV N°1 | 120 | 698 | Factor Kp | 120 | 835 | 120 | 954 | Probe N°1
| 699 | VAV N°2 |  | 699 | Factor Ki |  |  |  | 955 | Probe N°2
121 | 700 | VAV N°1 | 121 | 700 | Factor Kp | 121 | 836 | 121 | 956 | Probe N°1
| 701 | VAV N°2 |  | 701 | Factor Ki |  |  |  | 957 | Probe N°2
122 | 702 | VAV N°1 | 122 | 702 | Factor Kp | 122 | 837 | 122 | 958 | Probe N°1
| 703 | VAV N°2 |  | 703 | Factor Ki |  |  |  | 959 | Probe N°2
123 | 704 | VAV N°1 | 123 | 704 | Factor Kp | 123 | 838 | 123 | 960 | Probe N°1
| 705 | VAV N°2 |  | 705 | Factor Ki |  |  |  | 961 | Probe N°2
124 | 706 | VAV N°1 | 124 | 706 | Factor Kp | 124 | 839 | 124 | 962 | Probe N°1
| 707 | VAV N°2 |  | 707 | Factor Ki |  |  |  | 963 | Probe N°2
125 | 708 | VAV N°1 | 125 | 708 | Factor Kp | 125 | 840 | 125 | 964 | Probe N°1
| 709 | VAV N°2 |  | 709 | Factor Ki |  |  |  | 965 | Probe N°2
126 | 710 | VAV N°1 | 126 | 710 | Factor Kp | 126 | 841 | 126 | 966 | Probe N°1
| 711 | VAV N°2 |  | 711 | Factor Ki |  |  |  | 967 | Probe N°2
127 | 712 | VAV N°1 | 127 | 712 | Factor Kp | 127 | 842 | 127 | 968 | Probe N°1
| 713 | VAV N°2 |  | 713 | Factor Ki |  |  |  | 969 | Probe N°2
128 | 714 | VAV N°1 | 128 | 714 | Factor Kp | 128 | 843 | 128 | 970 | Probe N°1
| 715 | VAV N°2 |  | 715 | Factor Ki |  |  |  | 971 | Probe N°2

## EASY-IO
Easy-IO | [9 empty] | A = Output/Input A
B = Output/Input B
C = Output/Input C
D = Output/Input D
Easybus | modbus RTU |  |  |  |  | Easybus | modbus RTU |  |  |  |  | Easybus | modbus RTU
Address |  | Read (bits) |  |  |  | Address |  | Write (bits) |  |  |  | Address |  | Read (bits)
|  | D | C | B | A |  |  | D | C | B | A |  |  | Module error communication
1 | 426 | 3 | 2 | 1 | 0 | 1 | 324 | 3 | 2 | 1 | 0 | 1 | 300 | 0
2 |  | 7 | 6 | 5 | 4 | 2 |  | 7 | 6 | 5 | 4 | 2 |  | 4
3 |  | 11 | 10 | 9 | 8 | 3 |  | 11 | 10 | 9 | 8 | 3 |  | 8
4 |  | 15 | 14 | 13 | 12 | 4 |  | 15 | 14 | 13 | 12 | 4 |  | 12
5 | 427 | 3 | 2 | 1 | 0 | 5 | 325 | 3 | 2 | 1 | 0 | 5 | 301 | 0
6 |  | 7 | 6 | 5 | 4 | 6 |  | 7 | 6 | 5 | 4 | 6 |  | 4
7 |  | 11 | 10 | 9 | 8 | 7 |  | 11 | 10 | 9 | 8 | 7 |  | 8
8 |  | 15 | 14 | 13 | 12 | 8 |  | 15 | 14 | 13 | 12 | 8 |  | 12
9 | 428 | 3 | 2 | 1 | 0 | 9 | 326 | 3 | 2 | 1 | 0 | 9 | 302 | 0
10 |  | 7 | 6 | 5 | 4 | 10 |  | 7 | 6 | 5 | 4 | 10 |  | 4
11 |  | 11 | 10 | 9 | 8 | 11 |  | 11 | 10 | 9 | 8 | 11 |  | 8
12 |  | 15 | 14 | 13 | 12 | 12 |  | 15 | 14 | 13 | 12 | 12 |  | 12
13 | 429 | 3 | 2 | 1 | 0 | 13 | 327 | 3 | 2 | 1 | 0 | 13 | 303 | 0
14 |  | 7 | 6 | 5 | 4 | 14 |  | 7 | 6 | 5 | 4 | 14 |  | 4
15 |  | 11 | 10 | 9 | 8 | 15 |  | 11 | 10 | 9 | 8 | 15 |  | 8
16 |  | 15 | 14 | 13 | 12 | 16 |  | 15 | 14 | 13 | 12 | 16 |  | 12
17 | 430 | 3 | 2 | 1 | 0 | 17 | 328 | 3 | 2 | 1 | 0 | 17 | 304 | 0
18 |  | 7 | 6 | 5 | 4 | 18 |  | 7 | 6 | 5 | 4 | 18 |  | 4
19 |  | 11 | 10 | 9 | 8 | 19 |  | 11 | 10 | 9 | 8 | 19 |  | 8
20 |  | 15 | 14 | 13 | 12 | 20 |  | 15 | 14 | 13 | 12 | 20 |  | 12
21 | 431 | 3 | 2 | 1 | 0 | 21 | 329 | 3 | 2 | 1 | 0 | 21 | 305 | 0
22 |  | 7 | 6 | 5 | 4 | 22 |  | 7 | 6 | 5 | 4 | 22 |  | 4
23 |  | 11 | 10 | 9 | 8 | 23 |  | 11 | 10 | 9 | 8 | 23 |  | 8
24 |  | 15 | 14 | 13 | 12 | 24 |  | 15 | 14 | 13 | 12 | 24 |  | 12
25 | 432 | 3 | 2 | 1 | 0 | 25 | 330 | 3 | 2 | 1 | 0 | 25 | 306 | 0
26 |  | 7 | 6 | 5 | 4 | 26 |  | 7 | 6 | 5 | 4 | 26 |  | 4
27 |  | 11 | 10 | 9 | 8 | 27 |  | 11 | 10 | 9 | 8 | 27 |  | 8
28 |  | 15 | 14 | 13 | 12 | 28 |  | 15 | 14 | 13 | 12 | 28 |  | 12
29 | 433 | 3 | 2 | 1 | 0 | 29 | 331 | 3 | 2 | 1 | 0 | 29 | 307 | 0
30 |  | 7 | 6 | 5 | 4 | 30 |  | 7 | 6 | 5 | 4 | 30 |  | 4
31 |  | 11 | 10 | 9 | 8 | 31 |  | 11 | 10 | 9 | 8 | 31 |  | 8
32 |  | 15 | 14 | 13 | 12 | 32 |  | 15 | 14 | 13 | 12 | 32 |  | 12
33 | 434 | 3 | 2 | 1 | 0 | 33 | 332 | 3 | 2 | 1 | 0 | 33 | 308 | 0
34 |  | 7 | 6 | 5 | 4 | 34 |  | 7 | 6 | 5 | 4 | 34 |  | 4
35 |  | 11 | 10 | 9 | 8 | 35 |  | 11 | 10 | 9 | 8 | 35 |  | 8
36 |  | 15 | 14 | 13 | 12 | 36 |  | 15 | 14 | 13 | 12 | 36 |  | 12
37 | 435 | 3 | 2 | 1 | 0 | 37 | 333 | 3 | 2 | 1 | 0 | 37 | 309 | 0
38 |  | 7 | 6 | 5 | 4 | 38 |  | 7 | 6 | 5 | 4 | 38 |  | 4
39 |  | 11 | 10 | 9 | 8 | 39 |  | 11 | 10 | 9 | 8 | 39 |  | 8
40 |  | 15 | 14 | 13 | 12 | 40 |  | 15 | 14 | 13 | 12 | 40 |  | 12
41 | 436 | 3 | 2 | 1 | 0 | 41 | 334 | 3 | 2 | 1 | 0 | 41 | 310 | 0
42 |  | 7 | 6 | 5 | 4 | 42 |  | 7 | 6 | 5 | 4 | 42 |  | 4
43 |  | 11 | 10 | 9 | 8 | 43 |  | 11 | 10 | 9 | 8 | 43 |  | 8
44 |  | 15 | 14 | 13 | 12 | 44 |  | 15 | 14 | 13 | 12 | 44 |  | 12
45 | 437 | 3 | 2 | 1 | 0 | 45 | 335 | 3 | 2 | 1 | 0 | 45 | 311 | 0
46 |  | 7 | 6 | 5 | 4 | 46 |  | 7 | 6 | 5 | 4 | 46 |  | 4
47 |  | 11 | 10 | 9 | 8 | 47 |  | 11 | 10 | 9 | 8 | 47 |  | 8
48 |  | 15 | 14 | 13 | 12 | 48 |  | 15 | 14 | 13 | 12 | 48 |  | 12
49 | 438 | 3 | 2 | 1 | 0 | 49 | 336 | 3 | 2 | 1 | 0 | 49 | 312 | 0
50 |  | 7 | 6 | 5 | 4 | 50 |  | 7 | 6 | 5 | 4 | 50 |  | 4
51 |  | 11 | 10 | 9 | 8 | 51 |  | 11 | 10 | 9 | 8 | 51 |  | 8
52 |  | 15 | 14 | 13 | 12 | 52 |  | 15 | 14 | 13 | 12 | 52 |  | 12
53 | 439 | 3 | 2 | 1 | 0 | 53 | 337 | 3 | 2 | 1 | 0 | 53 | 313 | 0
54 |  | 7 | 6 | 5 | 4 | 54 |  | 7 | 6 | 5 | 4 | 54 |  | 4
55 |  | 11 | 10 | 9 | 8 | 55 |  | 11 | 10 | 9 | 8 | 55 |  | 8
56 |  | 15 | 14 | 13 | 12 | 56 |  | 15 | 14 | 13 | 12 | 56 |  | 12
57 | 440 | 3 | 2 | 1 | 0 | 57 | 338 | 3 | 2 | 1 | 0 | 57 | 314 | 0
58 |  | 7 | 6 | 5 | 4 | 58 |  | 7 | 6 | 5 | 4 | 58 |  | 4
59 |  | 11 | 10 | 9 | 8 | 59 |  | 11 | 10 | 9 | 8 | 59 |  | 8
60 |  | 15 | 14 | 13 | 12 | 60 |  | 15 | 14 | 13 | 12 | 60 |  | 12
61 | 441 | 3 | 2 | 1 | 0 | 61 | 339 | 3 | 2 | 1 | 0 | 61 | 315 | 0
62 |  | 7 | 6 | 5 | 4 | 62 |  | 7 | 6 | 5 | 4 | 62 |  | 4
63 |  | 11 | 10 | 9 | 8 | 63 |  | 11 | 10 | 9 | 8 | 63 |  | 8
64 |  | 15 | 14 | 13 | 12 | 64 |  | 15 | 14 | 13 | 12 | 64 |  | 12
65 | 442 | 3 | 2 | 1 | 0 | 65 | 340 | 3 | 2 | 1 | 0 | 65 | 316 | 0
66 |  | 7 | 6 | 5 | 4 | 66 |  | 7 | 6 | 5 | 4 | 66 |  | 4
67 |  | 11 | 10 | 9 | 8 | 67 |  | 11 | 10 | 9 | 8 | 67 |  | 8
68 |  | 15 | 14 | 13 | 12 | 68 |  | 15 | 14 | 13 | 12 | 68 |  | 12
69 | 443 | 3 | 2 | 1 | 0 | 69 | 341 | 3 | 2 | 1 | 0 | 69 | 317 | 0
70 |  | 7 | 6 | 5 | 4 | 70 |  | 7 | 6 | 5 | 4 | 70 |  | 4
71 |  | 11 | 10 | 9 | 8 | 71 |  | 11 | 10 | 9 | 8 | 71 |  | 8
72 |  | 15 | 14 | 13 | 12 | 72 |  | 15 | 14 | 13 | 12 | 72 |  | 12
73 | 444 | 3 | 2 | 1 | 0 | 73 | 342 | 3 | 2 | 1 | 0 | 73 | 318 | 0
74 |  | 7 | 6 | 5 | 4 | 74 |  | 7 | 6 | 5 | 4 | 74 |  | 4
75 |  | 11 | 10 | 9 | 8 | 75 |  | 11 | 10 | 9 | 8 | 75 |  | 8
76 |  | 15 | 14 | 13 | 12 | 76 |  | 15 | 14 | 13 | 12 | 76 |  | 12
77 | 445 | 3 | 2 | 1 | 0 | 77 | 343 | 3 | 2 | 1 | 0 | 77 | 319 | 0
78 |  | 7 | 6 | 5 | 4 | 78 |  | 7 | 6 | 5 | 4 | 78 |  | 4
79 |  | 11 | 10 | 9 | 8 | 79 |  | 11 | 10 | 9 | 8 | 79 |  | 8
80 |  | 15 | 14 | 13 | 12 | 80 |  | 15 | 14 | 13 | 12 | 80 |  | 12
81 | 446 | 3 | 2 | 1 | 0 | 81 | 344 | 3 | 2 | 1 | 0 | 81 | 320 | 0
82 |  | 7 | 6 | 5 | 4 | 82 |  | 7 | 6 | 5 | 4 | 82 |  | 4
83 |  | 11 | 10 | 9 | 8 | 83 |  | 11 | 10 | 9 | 8 | 83 |  | 8
84 |  | 15 | 14 | 13 | 12 | 84 |  | 15 | 14 | 13 | 12 | 84 |  | 12
85 | 447 | 3 | 2 | 1 | 0 | 85 | 345 | 3 | 2 | 1 | 0 | 85 | 321 | 0
86 |  | 7 | 6 | 5 | 4 | 86 |  | 7 | 6 | 5 | 4 | 86 |  | 4
87 |  | 11 | 10 | 9 | 8 | 87 |  | 11 | 10 | 9 | 8 | 87 |  | 8
88 |  | 15 | 14 | 13 | 12 | 88 |  | 15 | 14 | 13 | 12 | 88 |  | 12
89 | 448 | 3 | 2 | 1 | 0 | 89 | 346 | 3 | 2 | 1 | 0 | 89 | 322 | 0
90 |  | 7 | 6 | 5 | 4 | 90 |  | 7 | 6 | 5 | 4 | 90 |  | 4
91 |  | 11 | 10 | 9 | 8 | 91 |  | 11 | 10 | 9 | 8 | 91 |  | 8
92 |  | 15 | 14 | 13 | 12 | 92 |  | 15 | 14 | 13 | 12 | 92 |  | 12
93 | 449 | 3 | 2 | 1 | 0 | 93 | 347 | 3 | 2 | 1 | 0 | 93 | 323 | 0
94 |  | 7 | 6 | 5 | 4 | 94 |  | 7 | 6 | 5 | 4 | 94 |  | 4
95 |  | 11 | 10 | 9 | 8 | 95 |  | 11 | 10 | 9 | 8 | 95 |  | 8
96 |  | 15 | 14 | 13 | 12 | 96 |  | 15 | 14 | 13 | 12 | 96 |  | 12
97 | 450 | 3 | 2 | 1 | 0 | 97 | 348 | 3 | 2 | 1 | 0 | 97 | 324 | 0
98 |  | 7 | 6 | 5 | 4 | 98 |  | 7 | 6 | 5 | 4 | 98 |  | 4
99 |  | 11 | 10 | 9 | 8 | 99 |  | 11 | 10 | 9 | 8 | 99 |  | 8
100 |  | 15 | 14 | 13 | 12 | 100 |  | 15 | 14 | 13 | 12 | 100 |  | 12
101 | 451 | 3 | 2 | 1 | 0 | 101 | 349 | 3 | 2 | 1 | 0 | 101 | 325 | 0
102 |  | 7 | 6 | 5 | 4 | 102 |  | 7 | 6 | 5 | 4 | 102 |  | 4
103 |  | 11 | 10 | 9 | 8 | 103 |  | 11 | 10 | 9 | 8 | 103 |  | 8
104 |  | 15 | 14 | 13 | 12 | 104 |  | 15 | 14 | 13 | 12 | 104 |  | 12
105 | 452 | 3 | 2 | 1 | 0 | 105 | 350 | 3 | 2 | 1 | 0 | 105 | 326 | 0
106 |  | 7 | 6 | 5 | 4 | 106 |  | 7 | 6 | 5 | 4 | 106 |  | 4
107 |  | 11 | 10 | 9 | 8 | 107 |  | 11 | 10 | 9 | 8 | 107 |  | 8
108 |  | 15 | 14 | 13 | 12 | 108 |  | 15 | 14 | 13 | 12 | 108 |  | 12
109 | 453 | 3 | 2 | 1 | 0 | 109 | 351 | 3 | 2 | 1 | 0 | 109 | 327 | 0
110 |  | 7 | 6 | 5 | 4 | 110 |  | 7 | 6 | 5 | 4 | 110 |  | 4
111 |  | 11 | 10 | 9 | 8 | 111 |  | 11 | 10 | 9 | 8 | 111 |  | 8
112 |  | 15 | 14 | 13 | 12 | 112 |  | 15 | 14 | 13 | 12 | 112 |  | 12
113 | 454 | 3 | 2 | 1 | 0 | 113 | 352 | 3 | 2 | 1 | 0 | 113 | 328 | 0
114 |  | 7 | 6 | 5 | 4 | 114 |  | 7 | 6 | 5 | 4 | 114 |  | 4
115 |  | 11 | 10 | 9 | 8 | 115 |  | 11 | 10 | 9 | 8 | 115 |  | 8
116 |  | 15 | 14 | 13 | 12 | 116 |  | 15 | 14 | 13 | 12 | 116 |  | 12
117 | 455 | 3 | 2 | 1 | 0 | 117 | 353 | 3 | 2 | 1 | 0 | 117 | 329 | 0
118 |  | 7 | 6 | 5 | 4 | 118 |  | 7 | 6 | 5 | 4 | 118 |  | 4
119 |  | 11 | 10 | 9 | 8 | 119 |  | 11 | 10 | 9 | 8 | 119 |  | 8
120 |  | 15 | 14 | 13 | 12 | 120 |  | 15 | 14 | 13 | 12 | 120 |  | 12
121 | 456 | 3 | 2 | 1 | 0 | 121 | 354 | 3 | 2 | 1 | 0 | 121 | 330 | 0
122 |  | 7 | 6 | 5 | 4 | 122 |  | 7 | 6 | 5 | 4 | 122 |  | 4
123 |  | 11 | 10 | 9 | 8 | 123 |  | 11 | 10 | 9 | 8 | 123 |  | 8
124 |  | 15 | 14 | 13 | 12 | 124 |  | 15 | 14 | 13 | 12 | 124 |  | 12
125 | 457 | 3 | 2 | 1 | 0 | 125 | 355 | 3 | 2 | 1 | 0 | 125 | 331 | 0
126 |  | 7 | 6 | 5 | 4 | 126 |  | 7 | 6 | 5 | 4 | 126 |  | 4
127 |  | 11 | 10 | 9 | 8 | 127 |  | 11 | 10 | 9 | 8 | 127 |  | 8
128 |  | 15 | 14 | 13 | 12 | 128 |  | 15 | 14 | 13 | 12 | 128 |  | 12

## EASY-MP
Easy-MP
Error code
Bit 0 = Excessive utilisation
Bit 1 = Control range increased
Bit 2 = Overload
Bit 3 = Supercap malfunction
Easybus | modbus RTU |  | Easybus | modbus RTU |  | Easybus | modbus RTU |  | Easybus |  | modbus RTU |  | Easybus | modbus RTU |  | Easybus | modbus RTU |  | Easybus | modbus RTU |  | Easybus | modbus RTU
Address |  | Read Vnom [m3/h] | Address |  | Read flow [%] | Address |  | Read Position [%] | Address |  |  | Read Error code | Address |  | Write setpoint | Address |  | Write Min/Max | Address |  | Write Min/Max | Address |  | Read (bits)
|  | 0-65535 |  |  | 0-15000 |  |  | 0-10000 |  |  |  | 0-15 |  |  | 0-10000 |  |  | 0-10000 |  |  | 0-10000 |  |  | Module error communication
1 | 460 | VAV N°1 | 1 | 716 | VAV N°1 | 1 | 972 | VAV N°1 | 1 | 974 | LSB | VAV N°1 | 1 | 460 | VAV N°1 | 1 | 844 | VAV N°1 min | 65 | 1100 | VAV N°1 min | 1 | 300 | 0
| 461 | VAV N°2 |  | 717 | VAV N°2 |  | 973 | VAV N°2 |  |  | MSB | VAV N°2 |  | 461 | VAV N°2 |  | 845 | VAV N°1 max |  | 1101 | VAV N°1 max | 2 |  | 4
2 | 462 | VAV N°1 | 2 | 718 | VAV N°1 | 2 | 975 | VAV N°1 | 2 | 977 | LSB | VAV N°1 | 2 | 462 | VAV N°1 |  | 846 | VAV N°2 min |  | 1102 | VAV N°2 min | 3 |  | 8
| 463 | VAV N°2 |  | 719 | VAV N°2 |  | 976 | VAV N°2 |  |  | MSB | VAV N°2 |  | 463 | VAV N°2 |  | 847 | VAV N°2 max |  | 1103 | VAV N°2 max | 4 |  | 12
3 | 464 | VAV N°1 | 3 | 720 | VAV N°1 | 3 | 978 | VAV N°1 | 3 | 980 | LSB | VAV N°1 | 3 | 464 | VAV N°1 | 2 | 848 | VAV N°1 min | 66 | 1104 | VAV N°1 min | 5 | 301 | 0
| 465 | VAV N°2 |  | 721 | VAV N°2 |  | 979 | VAV N°2 |  |  | MSB | VAV N°2 |  | 465 | VAV N°2 |  | 849 | VAV N°1 max |  | 1105 | VAV N°1 max | 6 |  | 4
4 | 466 | VAV N°1 | 4 | 722 | VAV N°1 | 4 | 981 | VAV N°1 | 4 | 983 | LSB | VAV N°1 | 4 | 466 | VAV N°1 |  | 850 | VAV N°2 min |  | 1106 | VAV N°2 min | 7 |  | 8
| 467 | VAV N°2 |  | 723 | VAV N°2 |  | 982 | VAV N°2 |  |  | MSB | VAV N°2 |  | 467 | VAV N°2 |  | 851 | VAV N°2 max |  | 1107 | VAV N°2 max | 8 |  | 12
5 | 468 | VAV N°1 | 5 | 724 | VAV N°1 | 5 | 984 | VAV N°1 | 5 | 986 | LSB | VAV N°1 | 5 | 468 | VAV N°1 | 3 | 852 | VAV N°1 min | 67 | 1108 | VAV N°1 min | 9 | 302 | 0
| 469 | VAV N°2 |  | 725 | VAV N°2 |  | 985 | VAV N°2 |  |  | MSB | VAV N°2 |  | 469 | VAV N°2 |  | 853 | VAV N°1 max |  | 1109 | VAV N°1 max | 10 |  | 4
6 | 470 | VAV N°1 | 6 | 726 | VAV N°1 | 6 | 987 | VAV N°1 | 6 | 989 | LSB | VAV N°1 | 6 | 470 | VAV N°1 |  | 854 | VAV N°2 min |  | 1110 | VAV N°2 min | 11 |  | 8
| 471 | VAV N°2 |  | 727 | VAV N°2 |  | 988 | VAV N°2 |  |  | MSB | VAV N°2 |  | 471 | VAV N°2 |  | 855 | VAV N°2 max |  | 1111 | VAV N°2 max | 12 |  | 12
7 | 472 | VAV N°1 | 7 | 728 | VAV N°1 | 7 | 990 | VAV N°1 | 7 | 992 | LSB | VAV N°1 | 7 | 472 | VAV N°1 | 4 | 856 | VAV N°1 min | 68 | 1112 | VAV N°1 min | 13 | 303 | 0
| 473 | VAV N°2 |  | 729 | VAV N°2 |  | 991 | VAV N°2 |  |  | MSB | VAV N°2 |  | 473 | VAV N°2 |  | 857 | VAV N°1 max |  | 1113 | VAV N°1 max | 14 |  | 4
8 | 474 | VAV N°1 | 8 | 730 | VAV N°1 | 8 | 993 | VAV N°1 | 8 | 995 | LSB | VAV N°1 | 8 | 474 | VAV N°1 |  | 858 | VAV N°2 min |  | 1114 | VAV N°2 min | 15 |  | 8
| 475 | VAV N°2 |  | 731 | VAV N°2 |  | 994 | VAV N°2 |  |  | MSB | VAV N°2 |  | 475 | VAV N°2 |  | 859 | VAV N°2 max |  | 1115 | VAV N°2 max | 16 |  | 12
9 | 476 | VAV N°1 | 9 | 732 | VAV N°1 | 9 | 996 | VAV N°1 | 9 | 998 | LSB | VAV N°1 | 9 | 476 | VAV N°1 | 5 | 860 | VAV N°1 min | 69 | 1116 | VAV N°1 min | 17 | 304 | 0
| 477 | VAV N°2 |  | 733 | VAV N°2 |  | 997 | VAV N°2 |  |  | MSB | VAV N°2 |  | 477 | VAV N°2 |  | 861 | VAV N°1 max |  | 1117 | VAV N°1 max | 18 |  | 4
10 | 478 | VAV N°1 | 10 | 734 | VAV N°1 | 10 | 999 | VAV N°1 | 10 | 1001 | LSB | VAV N°1 | 10 | 478 | VAV N°1 |  | 862 | VAV N°2 min |  | 1118 | VAV N°2 min | 19 |  | 8
| 479 | VAV N°2 |  | 735 | VAV N°2 |  | 1000 | VAV N°2 |  |  | MSB | VAV N°2 |  | 479 | VAV N°2 |  | 863 | VAV N°2 max |  | 1119 | VAV N°2 max | 20 |  | 12
11 | 480 | VAV N°1 | 11 | 736 | VAV N°1 | 11 | 1002 | VAV N°1 | 11 | 975 | LSB | VAV N°1 | 11 | 480 | VAV N°1 | 6 | 864 | VAV N°1 min | 70 | 1120 | VAV N°1 min | 21 | 305 | 0
| 481 | VAV N°2 |  | 737 | VAV N°2 |  | 1003 | VAV N°2 |  |  | MSB | VAV N°2 |  | 481 | VAV N°2 |  | 865 | VAV N°1 max |  | 1121 | VAV N°1 max | 22 |  | 4
12 | 482 | VAV N°1 | 12 | 738 | VAV N°1 | 12 | 1005 | VAV N°1 | 12 | 978 | LSB | VAV N°1 | 12 | 482 | VAV N°1 |  | 866 | VAV N°2 min |  | 1122 | VAV N°2 min | 23 |  | 8
| 483 | VAV N°2 |  | 739 | VAV N°2 |  | 1006 | VAV N°2 |  |  | MSB | VAV N°2 |  | 483 | VAV N°2 |  | 867 | VAV N°2 max |  | 1123 | VAV N°2 max | 24 |  | 12
13 | 484 | VAV N°1 | 13 | 740 | VAV N°1 | 13 | 1008 | VAV N°1 | 13 | 981 | LSB | VAV N°1 | 13 | 484 | VAV N°1 | 7 | 868 | VAV N°1 min | 71 | 1124 | VAV N°1 min | 25 | 306 | 0
| 485 | VAV N°2 |  | 741 | VAV N°2 |  | 1009 | VAV N°2 |  |  | MSB | VAV N°2 |  | 485 | VAV N°2 |  | 869 | VAV N°1 max |  | 1125 | VAV N°1 max | 26 |  | 4
14 | 486 | VAV N°1 | 14 | 742 | VAV N°1 | 14 | 1011 | VAV N°1 | 14 | 984 | LSB | VAV N°1 | 14 | 486 | VAV N°1 |  | 870 | VAV N°2 min |  | 1126 | VAV N°2 min | 27 |  | 8
| 487 | VAV N°2 |  | 743 | VAV N°2 |  | 1012 | VAV N°2 |  |  | MSB | VAV N°2 |  | 487 | VAV N°2 |  | 871 | VAV N°2 max |  | 1127 | VAV N°2 max | 28 |  | 12
15 | 488 | VAV N°1 | 15 | 744 | VAV N°1 | 15 | 1014 | VAV N°1 | 15 | 987 | LSB | VAV N°1 | 15 | 488 | VAV N°1 | 8 | 872 | VAV N°1 min | 72 | 1128 | VAV N°1 min | 29 | 307 | 0
| 489 | VAV N°2 |  | 745 | VAV N°2 |  | 1015 | VAV N°2 |  |  | MSB | VAV N°2 |  | 489 | VAV N°2 |  | 873 | VAV N°1 max |  | 1129 | VAV N°1 max | 30 |  | 4
16 | 490 | VAV N°1 | 16 | 746 | VAV N°1 | 16 | 1017 | VAV N°1 | 16 | 990 | LSB | VAV N°1 | 16 | 490 | VAV N°1 |  | 874 | VAV N°2 min |  | 1130 | VAV N°2 min | 31 |  | 8
| 491 | VAV N°2 |  | 747 | VAV N°2 |  | 1018 | VAV N°2 |  |  | MSB | VAV N°2 |  | 491 | VAV N°2 |  | 875 | VAV N°2 max |  | 1131 | VAV N°2 max | 32 |  | 12
17 | 492 | VAV N°1 | 17 | 748 | VAV N°1 | 17 | 1020 | VAV N°1 | 17 | 993 | LSB | VAV N°1 | 17 | 492 | VAV N°1 | 9 | 876 | VAV N°1 min | 73 | 1132 | VAV N°1 min | 33 | 308 | 0
| 493 | VAV N°2 |  | 749 | VAV N°2 |  | 1021 | VAV N°2 |  |  | MSB | VAV N°2 |  | 493 | VAV N°2 |  | 877 | VAV N°1 max |  | 1133 | VAV N°1 max | 34 |  | 4
18 | 494 | VAV N°1 | 18 | 750 | VAV N°1 | 18 | 1023 | VAV N°1 | 18 | 996 | LSB | VAV N°1 | 18 | 494 | VAV N°1 |  | 878 | VAV N°2 min |  | 1134 | VAV N°2 min | 35 |  | 8
| 495 | VAV N°2 |  | 751 | VAV N°2 |  | 1024 | VAV N°2 |  |  | MSB | VAV N°2 |  | 495 | VAV N°2 |  | 879 | VAV N°2 max |  | 1135 | VAV N°2 max | 36 |  | 12
19 | 496 | VAV N°1 | 19 | 752 | VAV N°1 | 19 | 1026 | VAV N°1 | 19 | 999 | LSB | VAV N°1 | 19 | 496 | VAV N°1 | 10 | 880 | VAV N°1 min | 74 | 1136 | VAV N°1 min | 37 | 309 | 0
| 497 | VAV N°2 |  | 753 | VAV N°2 |  | 1027 | VAV N°2 |  |  | MSB | VAV N°2 |  | 497 | VAV N°2 |  | 881 | VAV N°1 max |  | 1137 | VAV N°1 max | 38 |  | 4
20 | 498 | VAV N°1 | 20 | 754 | VAV N°1 | 20 | 1029 | VAV N°1 | 20 | 1002 | LSB | VAV N°1 | 20 | 498 | VAV N°1 |  | 882 | VAV N°2 min |  | 1138 | VAV N°2 min | 39 |  | 8
| 499 | VAV N°2 |  | 755 | VAV N°2 |  | 1030 | VAV N°2 |  |  | MSB | VAV N°2 |  | 499 | VAV N°2 |  | 883 | VAV N°2 max |  | 1139 | VAV N°2 max | 40 |  | 12
21 | 500 | VAV N°1 | 21 | 756 | VAV N°1 | 21 | 1032 | VAV N°1 | 21 | 976 | LSB | VAV N°1 | 21 | 500 | VAV N°1 | 11 | 884 | VAV N°1 min | 75 | 1140 | VAV N°1 min | 41 | 310 | 0
| 501 | VAV N°2 |  | 757 | VAV N°2 |  | 1033 | VAV N°2 |  |  | MSB | VAV N°2 |  | 501 | VAV N°2 |  | 885 | VAV N°1 max |  | 1141 | VAV N°1 max | 42 |  | 4
22 | 502 | VAV N°1 | 22 | 758 | VAV N°1 | 22 | 1035 | VAV N°1 | 22 | 979 | LSB | VAV N°1 | 22 | 502 | VAV N°1 |  | 886 | VAV N°2 min |  | 1142 | VAV N°2 min | 43 |  | 8
| 503 | VAV N°2 |  | 759 | VAV N°2 |  | 1036 | VAV N°2 |  |  | MSB | VAV N°2 |  | 503 | VAV N°2 |  | 887 | VAV N°2 max |  | 1143 | VAV N°2 max | 44 |  | 12
23 | 504 | VAV N°1 | 23 | 760 | VAV N°1 | 23 | 1038 | VAV N°1 | 23 | 982 | LSB | VAV N°1 | 23 | 504 | VAV N°1 | 12 | 888 | VAV N°1 min | 76 | 1144 | VAV N°1 min | 45 | 311 | 0
| 505 | VAV N°2 |  | 761 | VAV N°2 |  | 1039 | VAV N°2 |  |  | MSB | VAV N°2 |  | 505 | VAV N°2 |  | 889 | VAV N°1 max |  | 1145 | VAV N°1 max | 46 |  | 4
24 | 506 | VAV N°1 | 24 | 762 | VAV N°1 | 24 | 1041 | VAV N°1 | 24 | 985 | LSB | VAV N°1 | 24 | 506 | VAV N°1 |  | 890 | VAV N°2 min |  | 1146 | VAV N°2 min | 47 |  | 8
| 507 | VAV N°2 |  | 763 | VAV N°2 |  | 1042 | VAV N°2 |  |  | MSB | VAV N°2 |  | 507 | VAV N°2 |  | 891 | VAV N°2 max |  | 1147 | VAV N°2 max | 48 |  | 12
25 | 508 | VAV N°1 | 25 | 764 | VAV N°1 | 25 | 1044 | VAV N°1 | 25 | 988 | LSB | VAV N°1 | 25 | 508 | VAV N°1 | 13 | 892 | VAV N°1 min | 77 | 1148 | VAV N°1 min | 49 | 312 | 0
| 509 | VAV N°2 |  | 765 | VAV N°2 |  | 1045 | VAV N°2 |  |  | MSB | VAV N°2 |  | 509 | VAV N°2 |  | 893 | VAV N°1 max |  | 1149 | VAV N°1 max | 50 |  | 4
26 | 510 | VAV N°1 | 26 | 766 | VAV N°1 | 26 | 1047 | VAV N°1 | 26 | 991 | LSB | VAV N°1 | 26 | 510 | VAV N°1 |  | 894 | VAV N°2 min |  | 1150 | VAV N°2 min | 51 |  | 8
| 511 | VAV N°2 |  | 767 | VAV N°2 |  | 1048 | VAV N°2 |  |  | MSB | VAV N°2 |  | 511 | VAV N°2 |  | 895 | VAV N°2 max |  | 1151 | VAV N°2 max | 52 |  | 12
27 | 512 | VAV N°1 | 27 | 768 | VAV N°1 | 27 | 1050 | VAV N°1 | 27 | 994 | LSB | VAV N°1 | 27 | 512 | VAV N°1 | 14 | 896 | VAV N°1 min | 78 | 1152 | VAV N°1 min | 53 | 313 | 0
| 513 | VAV N°2 |  | 769 | VAV N°2 |  | 1051 | VAV N°2 |  |  | MSB | VAV N°2 |  | 513 | VAV N°2 |  | 897 | VAV N°1 max |  | 1153 | VAV N°1 max | 54 |  | 4
28 | 514 | VAV N°1 | 28 | 770 | VAV N°1 | 28 | 1053 | VAV N°1 | 28 | 997 | LSB | VAV N°1 | 28 | 514 | VAV N°1 |  | 898 | VAV N°2 min |  | 1154 | VAV N°2 min | 55 |  | 8
| 515 | VAV N°2 |  | 771 | VAV N°2 |  | 1054 | VAV N°2 |  |  | MSB | VAV N°2 |  | 515 | VAV N°2 |  | 899 | VAV N°2 max |  | 1155 | VAV N°2 max | 56 |  | 12
29 | 516 | VAV N°1 | 29 | 772 | VAV N°1 | 29 | 1056 | VAV N°1 | 29 | 1000 | LSB | VAV N°1 | 29 | 516 | VAV N°1 | 15 | 900 | VAV N°1 min | 79 | 1156 | VAV N°1 min | 57 | 314 | 0
| 517 | VAV N°2 |  | 773 | VAV N°2 |  | 1057 | VAV N°2 |  |  | MSB | VAV N°2 |  | 517 | VAV N°2 |  | 901 | VAV N°1 max |  | 1157 | VAV N°1 max | 58 |  | 4
30 | 518 | VAV N°1 | 30 | 774 | VAV N°1 | 30 | 1059 | VAV N°1 | 30 | 1003 | LSB | VAV N°1 | 30 | 518 | VAV N°1 |  | 902 | VAV N°2 min |  | 1158 | VAV N°2 min | 59 |  | 8
| 519 | VAV N°2 |  | 775 | VAV N°2 |  | 1060 | VAV N°2 |  |  | MSB | VAV N°2 |  | 519 | VAV N°2 |  | 903 | VAV N°2 max |  | 1159 | VAV N°2 max | 60 |  | 12
31 | 520 | VAV N°1 | 31 | 776 | VAV N°1 | 31 | 1062 | VAV N°1 | 31 | 977 | LSB | VAV N°1 | 31 | 520 | VAV N°1 | 16 | 904 | VAV N°1 min | 80 | 1160 | VAV N°1 min | 61 | 315 | 0
| 521 | VAV N°2 |  | 777 | VAV N°2 |  | 1063 | VAV N°2 |  |  | MSB | VAV N°2 |  | 521 | VAV N°2 |  | 905 | VAV N°1 max |  | 1161 | VAV N°1 max | 62 |  | 4
32 | 522 | VAV N°1 | 32 | 778 | VAV N°1 | 32 | 1065 | VAV N°1 | 32 | 980 | LSB | VAV N°1 | 32 | 522 | VAV N°1 |  | 906 | VAV N°2 min |  | 1162 | VAV N°2 min | 63 |  | 8
| 523 | VAV N°2 |  | 779 | VAV N°2 |  | 1066 | VAV N°2 |  |  | MSB | VAV N°2 |  | 523 | VAV N°2 |  | 907 | VAV N°2 max |  | 1163 | VAV N°2 max | 64 |  | 12
33 | 524 | VAV N°1 | 33 | 780 | VAV N°1 | 33 | 1068 | VAV N°1 | 33 | 983 | LSB | VAV N°1 | 33 | 524 | VAV N°1 | 17 | 908 | VAV N°1 min | 81 | 1164 | VAV N°1 min | 65 | 316 | 0
| 525 | VAV N°2 |  | 781 | VAV N°2 |  | 1069 | VAV N°2 |  |  | MSB | VAV N°2 |  | 525 | VAV N°2 |  | 909 | VAV N°1 max |  | 1165 | VAV N°1 max | 66 |  | 4
34 | 526 | VAV N°1 | 34 | 782 | VAV N°1 | 34 | 1071 | VAV N°1 | 34 | 986 | LSB | VAV N°1 | 34 | 526 | VAV N°1 |  | 910 | VAV N°2 min |  | 1166 | VAV N°2 min | 67 |  | 8
| 527 | VAV N°2 |  | 783 | VAV N°2 |  | 1072 | VAV N°2 |  |  | MSB | VAV N°2 |  | 527 | VAV N°2 |  | 911 | VAV N°2 max |  | 1167 | VAV N°2 max | 68 |  | 12
35 | 528 | VAV N°1 | 35 | 784 | VAV N°1 | 35 | 1074 | VAV N°1 | 35 | 989 | LSB | VAV N°1 | 35 | 528 | VAV N°1 | 18 | 912 | VAV N°1 min | 82 | 1168 | VAV N°1 min | 69 | 317 | 0
| 529 | VAV N°2 |  | 785 | VAV N°2 |  | 1075 | VAV N°2 |  |  | MSB | VAV N°2 |  | 529 | VAV N°2 |  | 913 | VAV N°1 max |  | 1169 | VAV N°1 max | 70 |  | 4
36 | 530 | VAV N°1 | 36 | 786 | VAV N°1 | 36 | 1077 | VAV N°1 | 36 | 992 | LSB | VAV N°1 | 36 | 530 | VAV N°1 |  | 914 | VAV N°2 min |  | 1170 | VAV N°2 min | 71 |  | 8
| 531 | VAV N°2 |  | 787 | VAV N°2 |  | 1078 | VAV N°2 |  |  | MSB | VAV N°2 |  | 531 | VAV N°2 |  | 915 | VAV N°2 max |  | 1171 | VAV N°2 max | 72 |  | 12
37 | 532 | VAV N°1 | 37 | 788 | VAV N°1 | 37 | 1080 | VAV N°1 | 37 | 995 | LSB | VAV N°1 | 37 | 532 | VAV N°1 | 19 | 916 | VAV N°1 min | 83 | 1172 | VAV N°1 min | 73 | 318 | 0
| 533 | VAV N°2 |  | 789 | VAV N°2 |  | 1081 | VAV N°2 |  |  | MSB | VAV N°2 |  | 533 | VAV N°2 |  | 917 | VAV N°1 max |  | 1173 | VAV N°1 max | 74 |  | 4
38 | 534 | VAV N°1 | 38 | 790 | VAV N°1 | 38 | 1083 | VAV N°1 | 38 | 998 | LSB | VAV N°1 | 38 | 534 | VAV N°1 |  | 918 | VAV N°2 min |  | 1174 | VAV N°2 min | 75 |  | 8
| 535 | VAV N°2 |  | 791 | VAV N°2 |  | 1084 | VAV N°2 |  |  | MSB | VAV N°2 |  | 535 | VAV N°2 |  | 919 | VAV N°2 max |  | 1175 | VAV N°2 max | 76 |  | 12
39 | 536 | VAV N°1 | 39 | 792 | VAV N°1 | 39 | 1086 | VAV N°1 | 39 | 1001 | LSB | VAV N°1 | 39 | 536 | VAV N°1 | 20 | 920 | VAV N°1 min | 84 | 1176 | VAV N°1 min | 77 | 319 | 0
| 537 | VAV N°2 |  | 793 | VAV N°2 |  | 1087 | VAV N°2 |  |  | MSB | VAV N°2 |  | 537 | VAV N°2 |  | 921 | VAV N°1 max |  | 1177 | VAV N°1 max | 78 |  | 4
40 | 538 | VAV N°1 | 40 | 794 | VAV N°1 | 40 | 1089 | VAV N°1 | 40 | 1004 | LSB | VAV N°1 | 40 | 538 | VAV N°1 |  | 922 | VAV N°2 min |  | 1178 | VAV N°2 min | 79 |  | 8
| 539 | VAV N°2 |  | 795 | VAV N°2 |  | 1090 | VAV N°2 |  |  | MSB | VAV N°2 |  | 539 | VAV N°2 |  | 923 | VAV N°2 max |  | 1179 | VAV N°2 max | 80 |  | 12
41 | 540 | VAV N°1 | 41 | 796 | VAV N°1 | 41 | 1092 | VAV N°1 | 41 | 978 | LSB | VAV N°1 | 41 | 540 | VAV N°1 | 21 | 924 | VAV N°1 min | 85 | 1180 | VAV N°1 min | 81 | 320 | 0
| 541 | VAV N°2 |  | 797 | VAV N°2 |  | 1093 | VAV N°2 |  |  | MSB | VAV N°2 |  | 541 | VAV N°2 |  | 925 | VAV N°1 max |  | 1181 | VAV N°1 max | 82 |  | 4
42 | 542 | VAV N°1 | 42 | 798 | VAV N°1 | 42 | 1095 | VAV N°1 | 42 | 981 | LSB | VAV N°1 | 42 | 542 | VAV N°1 |  | 926 | VAV N°2 min |  | 1182 | VAV N°2 min | 83 |  | 8
| 543 | VAV N°2 |  | 799 | VAV N°2 |  | 1096 | VAV N°2 |  |  | MSB | VAV N°2 |  | 543 | VAV N°2 |  | 927 | VAV N°2 max |  | 1183 | VAV N°2 max | 84 |  | 12
43 | 544 | VAV N°1 | 43 | 800 | VAV N°1 | 43 | 1098 | VAV N°1 | 43 | 984 | LSB | VAV N°1 | 43 | 544 | VAV N°1 | 22 | 928 | VAV N°1 min | 86 | 1184 | VAV N°1 min | 85 | 321 | 0
| 545 | VAV N°2 |  | 801 | VAV N°2 |  | 1099 | VAV N°2 |  |  | MSB | VAV N°2 |  | 545 | VAV N°2 |  | 929 | VAV N°1 max |  | 1185 | VAV N°1 max | 86 |  | 4
44 | 546 | VAV N°1 | 44 | 802 | VAV N°1 | 44 | 1101 | VAV N°1 | 44 | 987 | LSB | VAV N°1 | 44 | 546 | VAV N°1 |  | 930 | VAV N°2 min |  | 1186 | VAV N°2 min | 87 |  | 8
| 547 | VAV N°2 |  | 803 | VAV N°2 |  | 1102 | VAV N°2 |  |  | MSB | VAV N°2 |  | 547 | VAV N°2 |  | 931 | VAV N°2 max |  | 1187 | VAV N°2 max | 88 |  | 12
45 | 548 | VAV N°1 | 45 | 804 | VAV N°1 | 45 | 1104 | VAV N°1 | 45 | 990 | LSB | VAV N°1 | 45 | 548 | VAV N°1 | 23 | 932 | VAV N°1 min | 87 | 1188 | VAV N°1 min | 89 | 322 | 0
| 549 | VAV N°2 |  | 805 | VAV N°2 |  | 1105 | VAV N°2 |  |  | MSB | VAV N°2 |  | 549 | VAV N°2 |  | 933 | VAV N°1 max |  | 1189 | VAV N°1 max | 90 |  | 4
46 | 550 | VAV N°1 | 46 | 806 | VAV N°1 | 46 | 1107 | VAV N°1 | 46 | 993 | LSB | VAV N°1 | 46 | 550 | VAV N°1 |  | 934 | VAV N°2 min |  | 1190 | VAV N°2 min | 91 |  | 8
| 551 | VAV N°2 |  | 807 | VAV N°2 |  | 1108 | VAV N°2 |  |  | MSB | VAV N°2 |  | 551 | VAV N°2 |  | 935 | VAV N°2 max |  | 1191 | VAV N°2 max | 92 |  | 12
47 | 552 | VAV N°1 | 47 | 808 | VAV N°1 | 47 | 1110 | VAV N°1 | 47 | 996 | LSB | VAV N°1 | 47 | 552 | VAV N°1 | 24 | 936 | VAV N°1 min | 88 | 1192 | VAV N°1 min | 93 | 323 | 0
| 553 | VAV N°2 |  | 809 | VAV N°2 |  | 1111 | VAV N°2 |  |  | MSB | VAV N°2 |  | 553 | VAV N°2 |  | 937 | VAV N°1 max |  | 1193 | VAV N°1 max | 94 |  | 4
48 | 554 | VAV N°1 | 48 | 810 | VAV N°1 | 48 | 1113 | VAV N°1 | 48 | 999 | LSB | VAV N°1 | 48 | 554 | VAV N°1 |  | 938 | VAV N°2 min |  | 1194 | VAV N°2 min | 95 |  | 8
| 555 | VAV N°2 |  | 811 | VAV N°2 |  | 1114 | VAV N°2 |  |  | MSB | VAV N°2 |  | 555 | VAV N°2 |  | 939 | VAV N°2 max |  | 1195 | VAV N°2 max | 96 |  | 12
49 | 556 | VAV N°1 | 49 | 812 | VAV N°1 | 49 | 1116 | VAV N°1 | 49 | 1002 | LSB | VAV N°1 | 49 | 556 | VAV N°1 | 25 | 940 | VAV N°1 min | 89 | 1196 | VAV N°1 min | 97 | 324 | 0
| 557 | VAV N°2 |  | 813 | VAV N°2 |  | 1117 | VAV N°2 |  |  | MSB | VAV N°2 |  | 557 | VAV N°2 |  | 941 | VAV N°1 max |  | 1197 | VAV N°1 max | 98 |  | 4
50 | 558 | VAV N°1 | 50 | 814 | VAV N°1 | 50 | 1119 | VAV N°1 | 50 | 1005 | LSB | VAV N°1 | 50 | 558 | VAV N°1 |  | 942 | VAV N°2 min |  | 1198 | VAV N°2 min | 99 |  | 8
| 559 | VAV N°2 |  | 815 | VAV N°2 |  | 1120 | VAV N°2 |  |  | MSB | VAV N°2 |  | 559 | VAV N°2 |  | 943 | VAV N°2 max |  | 1199 | VAV N°2 max | 100 |  | 12
51 | 560 | VAV N°1 | 51 | 816 | VAV N°1 | 51 | 1122 | VAV N°1 | 51 | 979 | LSB | VAV N°1 | 51 | 560 | VAV N°1 | 26 | 944 | VAV N°1 min | 90 | 1200 | VAV N°1 min | 101 | 325 | 0
| 561 | VAV N°2 |  | 817 | VAV N°2 |  | 1123 | VAV N°2 |  |  | MSB | VAV N°2 |  | 561 | VAV N°2 |  | 945 | VAV N°1 max |  | 1201 | VAV N°1 max | 102 |  | 4
52 | 562 | VAV N°1 | 52 | 818 | VAV N°1 | 52 | 1125 | VAV N°1 | 52 | 982 | LSB | VAV N°1 | 52 | 562 | VAV N°1 |  | 946 | VAV N°2 min |  | 1202 | VAV N°2 min | 103 |  | 8
| 563 | VAV N°2 |  | 819 | VAV N°2 |  | 1126 | VAV N°2 |  |  | MSB | VAV N°2 |  | 563 | VAV N°2 |  | 947 | VAV N°2 max |  | 1203 | VAV N°2 max | 104 |  | 12
53 | 564 | VAV N°1 | 53 | 820 | VAV N°1 | 53 | 1128 | VAV N°1 | 53 | 985 | LSB | VAV N°1 | 53 | 564 | VAV N°1 | 27 | 948 | VAV N°1 min | 91 | 1204 | VAV N°1 min | 105 | 326 | 0
| 565 | VAV N°2 |  | 821 | VAV N°2 |  | 1129 | VAV N°2 |  |  | MSB | VAV N°2 |  | 565 | VAV N°2 |  | 949 | VAV N°1 max |  | 1205 | VAV N°1 max | 106 |  | 4
54 | 566 | VAV N°1 | 54 | 822 | VAV N°1 | 54 | 1131 | VAV N°1 | 54 | 988 | LSB | VAV N°1 | 54 | 566 | VAV N°1 |  | 950 | VAV N°2 min |  | 1206 | VAV N°2 min | 107 |  | 8
| 567 | VAV N°2 |  | 823 | VAV N°2 |  | 1132 | VAV N°2 |  |  | MSB | VAV N°2 |  | 567 | VAV N°2 |  | 951 | VAV N°2 max |  | 1207 | VAV N°2 max | 108 |  | 12
55 | 568 | VAV N°1 | 55 | 824 | VAV N°1 | 55 | 1134 | VAV N°1 | 55 | 991 | LSB | VAV N°1 | 55 | 568 | VAV N°1 | 28 | 952 | VAV N°1 min | 92 | 1208 | VAV N°1 min | 109 | 327 | 0
| 569 | VAV N°2 |  | 825 | VAV N°2 |  | 1135 | VAV N°2 |  |  | MSB | VAV N°2 |  | 569 | VAV N°2 |  | 953 | VAV N°1 max |  | 1209 | VAV N°1 max | 110 |  | 4
56 | 570 | VAV N°1 | 56 | 826 | VAV N°1 | 56 | 1137 | VAV N°1 | 56 | 994 | LSB | VAV N°1 | 56 | 570 | VAV N°1 |  | 954 | VAV N°2 min |  | 1210 | VAV N°2 min | 111 |  | 8
| 571 | VAV N°2 |  | 827 | VAV N°2 |  | 1138 | VAV N°2 |  |  | MSB | VAV N°2 |  | 571 | VAV N°2 |  | 955 | VAV N°2 max |  | 1211 | VAV N°2 max | 112 |  | 12
57 | 572 | VAV N°1 | 57 | 828 | VAV N°1 | 57 | 1140 | VAV N°1 | 57 | 997 | LSB | VAV N°1 | 57 | 572 | VAV N°1 | 29 | 956 | VAV N°1 min | 93 | 1212 | VAV N°1 min | 113 | 328 | 0
| 573 | VAV N°2 |  | 829 | VAV N°2 |  | 1141 | VAV N°2 |  |  | MSB | VAV N°2 |  | 573 | VAV N°2 |  | 957 | VAV N°1 max |  | 1213 | VAV N°1 max | 114 |  | 4
58 | 574 | VAV N°1 | 58 | 830 | VAV N°1 | 58 | 1143 | VAV N°1 | 58 | 1000 | LSB | VAV N°1 | 58 | 574 | VAV N°1 |  | 958 | VAV N°2 min |  | 1214 | VAV N°2 min | 115 |  | 8
| 575 | VAV N°2 |  | 831 | VAV N°2 |  | 1144 | VAV N°2 |  |  | MSB | VAV N°2 |  | 575 | VAV N°2 |  | 959 | VAV N°2 max |  | 1215 | VAV N°2 max | 116 |  | 12
59 | 576 | VAV N°1 | 59 | 832 | VAV N°1 | 59 | 1146 | VAV N°1 | 59 | 1003 | LSB | VAV N°1 | 59 | 576 | VAV N°1 | 30 | 960 | VAV N°1 min | 94 | 1216 | VAV N°1 min | 117 | 329 | 0
| 577 | VAV N°2 |  | 833 | VAV N°2 |  | 1147 | VAV N°2 |  |  | MSB | VAV N°2 |  | 577 | VAV N°2 |  | 961 | VAV N°1 max |  | 1217 | VAV N°1 max | 118 |  | 4
60 | 578 | VAV N°1 | 60 | 834 | VAV N°1 | 60 | 1149 | VAV N°1 | 60 | 1006 | LSB | VAV N°1 | 60 | 578 | VAV N°1 |  | 962 | VAV N°2 min |  | 1218 | VAV N°2 min | 119 |  | 8
| 579 | VAV N°2 |  | 835 | VAV N°2 |  | 1150 | VAV N°2 |  |  | MSB | VAV N°2 |  | 579 | VAV N°2 |  | 963 | VAV N°2 max |  | 1219 | VAV N°2 max | 120 |  | 12
61 | 580 | VAV N°1 | 61 | 836 | VAV N°1 | 61 | 1152 | VAV N°1 | 61 | 980 | LSB | VAV N°1 | 61 | 580 | VAV N°1 | 31 | 964 | VAV N°1 min | 95 | 1220 | VAV N°1 min | 121 | 330 | 0
| 581 | VAV N°2 |  | 837 | VAV N°2 |  | 1153 | VAV N°2 |  |  | MSB | VAV N°2 |  | 581 | VAV N°2 |  | 965 | VAV N°1 max |  | 1221 | VAV N°1 max | 122 |  | 4
62 | 582 | VAV N°1 | 62 | 838 | VAV N°1 | 62 | 1155 | VAV N°1 | 62 | 983 | LSB | VAV N°1 | 62 | 582 | VAV N°1 |  | 966 | VAV N°2 min |  | 1222 | VAV N°2 min | 123 |  | 8
| 583 | VAV N°2 |  | 839 | VAV N°2 |  | 1156 | VAV N°2 |  |  | MSB | VAV N°2 |  | 583 | VAV N°2 |  | 967 | VAV N°2 max |  | 1223 | VAV N°2 max | 124 |  | 12
63 | 584 | VAV N°1 | 63 | 840 | VAV N°1 | 63 | 1158 | VAV N°1 | 63 | 986 | LSB | VAV N°1 | 63 | 584 | VAV N°1 | 32 | 968 | VAV N°1 min | 96 | 1224 | VAV N°1 min | 125 | 331 | 0
| 585 | VAV N°2 |  | 841 | VAV N°2 |  | 1159 | VAV N°2 |  |  | MSB | VAV N°2 |  | 585 | VAV N°2 |  | 969 | VAV N°1 max |  | 1225 | VAV N°1 max | 126 |  | 4
64 | 586 | VAV N°1 | 64 | 842 | VAV N°1 | 64 | 1161 | VAV N°1 | 64 | 989 | LSB | VAV N°1 | 64 | 586 | VAV N°1 |  | 970 | VAV N°2 min |  | 1226 | VAV N°2 min | 127 |  | 8
| 587 | VAV N°2 |  | 843 | VAV N°2 |  | 1162 | VAV N°2 |  |  | MSB | VAV N°2 |  | 587 | VAV N°2 |  | 971 | VAV N°2 max |  | 1227 | VAV N°2 max | 128 |  | 12
65 | 588 | VAV N°1 | 65 | 844 | VAV N°1 | 65 | 1164 | VAV N°1 | 65 | 992 | LSB | VAV N°1 | 65 | 588 | VAV N°1 | 33 | 972 | VAV N°1 min | 97 | 1228 | VAV N°1 min
| 589 | VAV N°2 |  | 845 | VAV N°2 |  | 1165 | VAV N°2 |  |  | MSB | VAV N°2 |  | 589 | VAV N°2 |  | 973 | VAV N°1 max |  | 1229 | VAV N°1 max
66 | 590 | VAV N°1 | 66 | 846 | VAV N°1 | 66 | 1167 | VAV N°1 | 66 | 995 | LSB | VAV N°1 | 66 | 590 | VAV N°1 |  | 974 | VAV N°2 min |  | 1230 | VAV N°2 min
| 591 | VAV N°2 |  | 847 | VAV N°2 |  | 1168 | VAV N°2 |  |  | MSB | VAV N°2 |  | 591 | VAV N°2 |  | 975 | VAV N°2 max |  | 1231 | VAV N°2 max
67 | 592 | VAV N°1 | 67 | 848 | VAV N°1 | 67 | 1170 | VAV N°1 | 67 | 998 | LSB | VAV N°1 | 67 | 592 | VAV N°1 | 34 | 976 | VAV N°1 min | 98 | 1232 | VAV N°1 min
| 593 | VAV N°2 |  | 849 | VAV N°2 |  | 1171 | VAV N°2 |  |  | MSB | VAV N°2 |  | 593 | VAV N°2 |  | 977 | VAV N°1 max |  | 1233 | VAV N°1 max
68 | 594 | VAV N°1 | 68 | 850 | VAV N°1 | 68 | 1173 | VAV N°1 | 68 | 1001 | LSB | VAV N°1 | 68 | 594 | VAV N°1 |  | 978 | VAV N°2 min |  | 1234 | VAV N°2 min
| 595 | VAV N°2 |  | 851 | VAV N°2 |  | 1174 | VAV N°2 |  |  | MSB | VAV N°2 |  | 595 | VAV N°2 |  | 979 | VAV N°2 max |  | 1235 | VAV N°2 max
69 | 596 | VAV N°1 | 69 | 852 | VAV N°1 | 69 | 1176 | VAV N°1 | 69 | 1004 | LSB | VAV N°1 | 69 | 596 | VAV N°1 | 35 | 980 | VAV N°1 min | 99 | 1236 | VAV N°1 min
| 597 | VAV N°2 |  | 853 | VAV N°2 |  | 1177 | VAV N°2 |  |  | MSB | VAV N°2 |  | 597 | VAV N°2 |  | 981 | VAV N°1 max |  | 1237 | VAV N°1 max
70 | 598 | VAV N°1 | 70 | 854 | VAV N°1 | 70 | 1179 | VAV N°1 | 70 | 1007 | LSB | VAV N°1 | 70 | 598 | VAV N°1 |  | 982 | VAV N°2 min |  | 1238 | VAV N°2 min
| 599 | VAV N°2 |  | 855 | VAV N°2 |  | 1180 | VAV N°2 |  |  | MSB | VAV N°2 |  | 599 | VAV N°2 |  | 983 | VAV N°2 max |  | 1239 | VAV N°2 max
71 | 600 | VAV N°1 | 71 | 856 | VAV N°1 | 71 | 1182 | VAV N°1 | 71 | 981 | LSB | VAV N°1 | 71 | 600 | VAV N°1 | 36 | 984 | VAV N°1 min | 100 | 1240 | VAV N°1 min
| 601 | VAV N°2 |  | 857 | VAV N°2 |  | 1183 | VAV N°2 |  |  | MSB | VAV N°2 |  | 601 | VAV N°2 |  | 985 | VAV N°1 max |  | 1241 | VAV N°1 max
72 | 602 | VAV N°1 | 72 | 858 | VAV N°1 | 72 | 1185 | VAV N°1 | 72 | 984 | LSB | VAV N°1 | 72 | 602 | VAV N°1 |  | 986 | VAV N°2 min |  | 1242 | VAV N°2 min
| 603 | VAV N°2 |  | 859 | VAV N°2 |  | 1186 | VAV N°2 |  |  | MSB | VAV N°2 |  | 603 | VAV N°2 |  | 987 | VAV N°2 max |  | 1243 | VAV N°2 max
73 | 604 | VAV N°1 | 73 | 860 | VAV N°1 | 73 | 1188 | VAV N°1 | 73 | 987 | LSB | VAV N°1 | 73 | 604 | VAV N°1 | 37 | 988 | VAV N°1 min | 101 | 1244 | VAV N°1 min
| 605 | VAV N°2 |  | 861 | VAV N°2 |  | 1189 | VAV N°2 |  |  | MSB | VAV N°2 |  | 605 | VAV N°2 |  | 989 | VAV N°1 max |  | 1245 | VAV N°1 max
74 | 606 | VAV N°1 | 74 | 862 | VAV N°1 | 74 | 1191 | VAV N°1 | 74 | 990 | LSB | VAV N°1 | 74 | 606 | VAV N°1 |  | 990 | VAV N°2 min |  | 1246 | VAV N°2 min
| 607 | VAV N°2 |  | 863 | VAV N°2 |  | 1192 | VAV N°2 |  |  | MSB | VAV N°2 |  | 607 | VAV N°2 |  | 991 | VAV N°2 max |  | 1247 | VAV N°2 max
75 | 608 | VAV N°1 | 75 | 864 | VAV N°1 | 75 | 1194 | VAV N°1 | 75 | 993 | LSB | VAV N°1 | 75 | 608 | VAV N°1 | 38 | 992 | VAV N°1 min | 102 | 1248 | VAV N°1 min
| 609 | VAV N°2 |  | 865 | VAV N°2 |  | 1195 | VAV N°2 |  |  | MSB | VAV N°2 |  | 609 | VAV N°2 |  | 993 | VAV N°1 max |  | 1249 | VAV N°1 max
76 | 610 | VAV N°1 | 76 | 866 | VAV N°1 | 76 | 1197 | VAV N°1 | 76 | 996 | LSB | VAV N°1 | 76 | 610 | VAV N°1 |  | 994 | VAV N°2 min |  | 1250 | VAV N°2 min
| 611 | VAV N°2 |  | 867 | VAV N°2 |  | 1198 | VAV N°2 |  |  | MSB | VAV N°2 |  | 611 | VAV N°2 |  | 995 | VAV N°2 max |  | 1251 | VAV N°2 max
77 | 612 | VAV N°1 | 77 | 868 | VAV N°1 | 77 | 1200 | VAV N°1 | 77 | 999 | LSB | VAV N°1 | 77 | 612 | VAV N°1 | 39 | 996 | VAV N°1 min | 103 | 1252 | VAV N°1 min
| 613 | VAV N°2 |  | 869 | VAV N°2 |  | 1201 | VAV N°2 |  |  | MSB | VAV N°2 |  | 613 | VAV N°2 |  | 997 | VAV N°1 max |  | 1253 | VAV N°1 max
78 | 614 | VAV N°1 | 78 | 870 | VAV N°1 | 78 | 1203 | VAV N°1 | 78 | 1002 | LSB | VAV N°1 | 78 | 614 | VAV N°1 |  | 998 | VAV N°2 min |  | 1254 | VAV N°2 min
| 615 | VAV N°2 |  | 871 | VAV N°2 |  | 1204 | VAV N°2 |  |  | MSB | VAV N°2 |  | 615 | VAV N°2 |  | 999 | VAV N°2 max |  | 1255 | VAV N°2 max
79 | 616 | VAV N°1 | 79 | 872 | VAV N°1 | 79 | 1206 | VAV N°1 | 79 | 1005 | LSB | VAV N°1 | 79 | 616 | VAV N°1 | 40 | 1000 | VAV N°1 min | 104 | 1256 | VAV N°1 min
| 617 | VAV N°2 |  | 873 | VAV N°2 |  | 1207 | VAV N°2 |  |  | MSB | VAV N°2 |  | 617 | VAV N°2 |  | 1001 | VAV N°1 max |  | 1257 | VAV N°1 max
80 | 618 | VAV N°1 | 80 | 874 | VAV N°1 | 80 | 1209 | VAV N°1 | 80 | 1008 | LSB | VAV N°1 | 80 | 618 | VAV N°1 |  | 1002 | VAV N°2 min |  | 1258 | VAV N°2 min
| 619 | VAV N°2 |  | 875 | VAV N°2 |  | 1210 | VAV N°2 |  |  | MSB | VAV N°2 |  | 619 | VAV N°2 |  | 1003 | VAV N°2 max |  | 1259 | VAV N°2 max
81 | 620 | VAV N°1 | 81 | 876 | VAV N°1 | 81 | 1212 | VAV N°1 | 81 | 982 | LSB | VAV N°1 | 81 | 620 | VAV N°1 | 41 | 1004 | VAV N°1 min | 105 | 1260 | VAV N°1 min
| 621 | VAV N°2 |  | 877 | VAV N°2 |  | 1213 | VAV N°2 |  |  | MSB | VAV N°2 |  | 621 | VAV N°2 |  | 1005 | VAV N°1 max |  | 1261 | VAV N°1 max
82 | 622 | VAV N°1 | 82 | 878 | VAV N°1 | 82 | 1215 | VAV N°1 | 82 | 985 | LSB | VAV N°1 | 82 | 622 | VAV N°1 |  | 1006 | VAV N°2 min |  | 1262 | VAV N°2 min
| 623 | VAV N°2 |  | 879 | VAV N°2 |  | 1216 | VAV N°2 |  |  | MSB | VAV N°2 |  | 623 | VAV N°2 |  | 1007 | VAV N°2 max |  | 1263 | VAV N°2 max
83 | 624 | VAV N°1 | 83 | 880 | VAV N°1 | 83 | 1218 | VAV N°1 | 83 | 988 | LSB | VAV N°1 | 83 | 624 | VAV N°1 | 42 | 1008 | VAV N°1 min | 106 | 1264 | VAV N°1 min
| 625 | VAV N°2 |  | 881 | VAV N°2 |  | 1219 | VAV N°2 |  |  | MSB | VAV N°2 |  | 625 | VAV N°2 |  | 1009 | VAV N°1 max |  | 1265 | VAV N°1 max
84 | 626 | VAV N°1 | 84 | 882 | VAV N°1 | 84 | 1221 | VAV N°1 | 84 | 991 | LSB | VAV N°1 | 84 | 626 | VAV N°1 |  | 1010 | VAV N°2 min |  | 1266 | VAV N°2 min
| 627 | VAV N°2 |  | 883 | VAV N°2 |  | 1222 | VAV N°2 |  |  | MSB | VAV N°2 |  | 627 | VAV N°2 |  | 1011 | VAV N°2 max |  | 1267 | VAV N°2 max
85 | 628 | VAV N°1 | 85 | 884 | VAV N°1 | 85 | 1224 | VAV N°1 | 85 | 994 | LSB | VAV N°1 | 85 | 628 | VAV N°1 | 43 | 1012 | VAV N°1 min | 107 | 1268 | VAV N°1 min
| 629 | VAV N°2 |  | 885 | VAV N°2 |  | 1225 | VAV N°2 |  |  | MSB | VAV N°2 |  | 629 | VAV N°2 |  | 1013 | VAV N°1 max |  | 1269 | VAV N°1 max
86 | 630 | VAV N°1 | 86 | 886 | VAV N°1 | 86 | 1227 | VAV N°1 | 86 | 997 | LSB | VAV N°1 | 86 | 630 | VAV N°1 |  | 1014 | VAV N°2 min |  | 1270 | VAV N°2 min
| 631 | VAV N°2 |  | 887 | VAV N°2 |  | 1228 | VAV N°2 |  |  | MSB | VAV N°2 |  | 631 | VAV N°2 |  | 1015 | VAV N°2 max |  | 1271 | VAV N°2 max
87 | 632 | VAV N°1 | 87 | 888 | VAV N°1 | 87 | 1230 | VAV N°1 | 87 | 1000 | LSB | VAV N°1 | 87 | 632 | VAV N°1 | 44 | 1016 | VAV N°1 min | 108 | 1272 | VAV N°1 min
| 633 | VAV N°2 |  | 889 | VAV N°2 |  | 1231 | VAV N°2 |  |  | MSB | VAV N°2 |  | 633 | VAV N°2 |  | 1017 | VAV N°1 max |  | 1273 | VAV N°1 max
88 | 634 | VAV N°1 | 88 | 890 | VAV N°1 | 88 | 1233 | VAV N°1 | 88 | 1003 | LSB | VAV N°1 | 88 | 634 | VAV N°1 |  | 1018 | VAV N°2 min |  | 1274 | VAV N°2 min
| 635 | VAV N°2 |  | 891 | VAV N°2 |  | 1234 | VAV N°2 |  |  | MSB | VAV N°2 |  | 635 | VAV N°2 |  | 1019 | VAV N°2 max |  | 1275 | VAV N°2 max
89 | 636 | VAV N°1 | 89 | 892 | VAV N°1 | 89 | 1236 | VAV N°1 | 89 | 1006 | LSB | VAV N°1 | 89 | 636 | VAV N°1 | 45 | 1020 | VAV N°1 min | 109 | 1276 | VAV N°1 min
| 637 | VAV N°2 |  | 893 | VAV N°2 |  | 1237 | VAV N°2 |  |  | MSB | VAV N°2 |  | 637 | VAV N°2 |  | 1021 | VAV N°1 max |  | 1277 | VAV N°1 max
90 | 638 | VAV N°1 | 90 | 894 | VAV N°1 | 90 | 1239 | VAV N°1 | 90 | 1009 | LSB | VAV N°1 | 90 | 638 | VAV N°1 |  | 1022 | VAV N°2 min |  | 1278 | VAV N°2 min
| 639 | VAV N°2 |  | 895 | VAV N°2 |  | 1240 | VAV N°2 |  |  | MSB | VAV N°2 |  | 639 | VAV N°2 |  | 1023 | VAV N°2 max |  | 1279 | VAV N°2 max
91 | 640 | VAV N°1 | 91 | 896 | VAV N°1 | 91 | 1242 | VAV N°1 | 91 | 983 | LSB | VAV N°1 | 91 | 640 | VAV N°1 | 46 | 1024 | VAV N°1 min | 110 | 1280 | VAV N°1 min
| 641 | VAV N°2 |  | 897 | VAV N°2 |  | 1243 | VAV N°2 |  |  | MSB | VAV N°2 |  | 641 | VAV N°2 |  | 1025 | VAV N°1 max |  | 1281 | VAV N°1 max
92 | 642 | VAV N°1 | 92 | 898 | VAV N°1 | 92 | 1245 | VAV N°1 | 92 | 986 | LSB | VAV N°1 | 92 | 642 | VAV N°1 |  | 1026 | VAV N°2 min |  | 1282 | VAV N°2 min
| 643 | VAV N°2 |  | 899 | VAV N°2 |  | 1246 | VAV N°2 |  |  | MSB | VAV N°2 |  | 643 | VAV N°2 |  | 1027 | VAV N°2 max |  | 1283 | VAV N°2 max
93 | 644 | VAV N°1 | 93 | 900 | VAV N°1 | 93 | 1248 | VAV N°1 | 93 | 989 | LSB | VAV N°1 | 93 | 644 | VAV N°1 | 47 | 1028 | VAV N°1 min | 111 | 1284 | VAV N°1 min
| 645 | VAV N°2 |  | 901 | VAV N°2 |  | 1249 | VAV N°2 |  |  | MSB | VAV N°2 |  | 645 | VAV N°2 |  | 1029 | VAV N°1 max |  | 1285 | VAV N°1 max
94 | 646 | VAV N°1 | 94 | 902 | VAV N°1 | 94 | 1251 | VAV N°1 | 94 | 992 | LSB | VAV N°1 | 94 | 646 | VAV N°1 |  | 1030 | VAV N°2 min |  | 1286 | VAV N°2 min
| 647 | VAV N°2 |  | 903 | VAV N°2 |  | 1252 | VAV N°2 |  |  | MSB | VAV N°2 |  | 647 | VAV N°2 |  | 1031 | VAV N°2 max |  | 1287 | VAV N°2 max
95 | 648 | VAV N°1 | 95 | 904 | VAV N°1 | 95 | 1254 | VAV N°1 | 95 | 995 | LSB | VAV N°1 | 95 | 648 | VAV N°1 | 48 | 1032 | VAV N°1 min | 112 | 1288 | VAV N°1 min
| 649 | VAV N°2 |  | 905 | VAV N°2 |  | 1255 | VAV N°2 |  |  | MSB | VAV N°2 |  | 649 | VAV N°2 |  | 1033 | VAV N°1 max |  | 1289 | VAV N°1 max
96 | 650 | VAV N°1 | 96 | 906 | VAV N°1 | 96 | 1257 | VAV N°1 | 96 | 998 | LSB | VAV N°1 | 96 | 650 | VAV N°1 |  | 1034 | VAV N°2 min |  | 1290 | VAV N°2 min
| 651 | VAV N°2 |  | 907 | VAV N°2 |  | 1258 | VAV N°2 |  |  | MSB | VAV N°2 |  | 651 | VAV N°2 |  | 1035 | VAV N°2 max |  | 1291 | VAV N°2 max
97 | 652 | VAV N°1 | 97 | 908 | VAV N°1 | 97 | 1260 | VAV N°1 | 97 | 1001 | LSB | VAV N°1 | 97 | 652 | VAV N°1 | 49 | 1036 | VAV N°1 min | 113 | 1292 | VAV N°1 min
| 653 | VAV N°2 |  | 909 | VAV N°2 |  | 1261 | VAV N°2 |  |  | MSB | VAV N°2 |  | 653 | VAV N°2 |  | 1037 | VAV N°1 max |  | 1293 | VAV N°1 max
98 | 654 | VAV N°1 | 98 | 910 | VAV N°1 | 98 | 1263 | VAV N°1 | 98 | 1004 | LSB | VAV N°1 | 98 | 654 | VAV N°1 |  | 1038 | VAV N°2 min |  | 1294 | VAV N°2 min
| 655 | VAV N°2 |  | 911 | VAV N°2 |  | 1264 | VAV N°2 |  |  | MSB | VAV N°2 |  | 655 | VAV N°2 |  | 1039 | VAV N°2 max |  | 1295 | VAV N°2 max
99 | 656 | VAV N°1 | 99 | 912 | VAV N°1 | 99 | 1266 | VAV N°1 | 99 | 1007 | LSB | VAV N°1 | 99 | 656 | VAV N°1 | 50 | 1040 | VAV N°1 min | 114 | 1296 | VAV N°1 min
| 657 | VAV N°2 |  | 913 | VAV N°2 |  | 1267 | VAV N°2 |  |  | MSB | VAV N°2 |  | 657 | VAV N°2 |  | 1041 | VAV N°1 max |  | 1297 | VAV N°1 max
100 | 658 | VAV N°1 | 100 | 914 | VAV N°1 | 100 | 1269 | VAV N°1 | 100 | 1010 | LSB | VAV N°1 | 100 | 658 | VAV N°1 |  | 1042 | VAV N°2 min |  | 1298 | VAV N°2 min
| 659 | VAV N°2 |  | 915 | VAV N°2 |  | 1270 | VAV N°2 |  |  | MSB | VAV N°2 |  | 659 | VAV N°2 |  | 1043 | VAV N°2 max |  | 1299 | VAV N°2 max
101 | 660 | VAV N°1 | 101 | 916 | VAV N°1 | 101 | 1272 | VAV N°1 | 101 | 984 | LSB | VAV N°1 | 101 | 660 | VAV N°1 | 51 | 1044 | VAV N°1 min | 115 | 1300 | VAV N°1 min
| 661 | VAV N°2 |  | 917 | VAV N°2 |  | 1273 | VAV N°2 |  |  | MSB | VAV N°2 |  | 661 | VAV N°2 |  | 1045 | VAV N°1 max |  | 1301 | VAV N°1 max
102 | 662 | VAV N°1 | 102 | 918 | VAV N°1 | 102 | 1275 | VAV N°1 | 102 | 987 | LSB | VAV N°1 | 102 | 662 | VAV N°1 |  | 1046 | VAV N°2 min |  | 1302 | VAV N°2 min
| 663 | VAV N°2 |  | 919 | VAV N°2 |  | 1276 | VAV N°2 |  |  | MSB | VAV N°2 |  | 663 | VAV N°2 |  | 1047 | VAV N°2 max |  | 1303 | VAV N°2 max
103 | 664 | VAV N°1 | 103 | 920 | VAV N°1 | 103 | 1278 | VAV N°1 | 103 | 990 | LSB | VAV N°1 | 103 | 664 | VAV N°1 | 52 | 1048 | VAV N°1 min | 116 | 1304 | VAV N°1 min
| 665 | VAV N°2 |  | 921 | VAV N°2 |  | 1279 | VAV N°2 |  |  | MSB | VAV N°2 |  | 665 | VAV N°2 |  | 1049 | VAV N°1 max |  | 1305 | VAV N°1 max
104 | 666 | VAV N°1 | 104 | 922 | VAV N°1 | 104 | 1281 | VAV N°1 | 104 | 993 | LSB | VAV N°1 | 104 | 666 | VAV N°1 |  | 1050 | VAV N°2 min |  | 1306 | VAV N°2 min
| 667 | VAV N°2 |  | 923 | VAV N°2 |  | 1282 | VAV N°2 |  |  | MSB | VAV N°2 |  | 667 | VAV N°2 |  | 1051 | VAV N°2 max |  | 1307 | VAV N°2 max
105 | 668 | VAV N°1 | 105 | 924 | VAV N°1 | 105 | 1284 | VAV N°1 | 105 | 996 | LSB | VAV N°1 | 105 | 668 | VAV N°1 | 53 | 1052 | VAV N°1 min | 117 | 1308 | VAV N°1 min
| 669 | VAV N°2 |  | 925 | VAV N°2 |  | 1285 | VAV N°2 |  |  | MSB | VAV N°2 |  | 669 | VAV N°2 |  | 1053 | VAV N°1 max |  | 1309 | VAV N°1 max
106 | 670 | VAV N°1 | 106 | 926 | VAV N°1 | 106 | 1287 | VAV N°1 | 106 | 999 | LSB | VAV N°1 | 106 | 670 | VAV N°1 |  | 1054 | VAV N°2 min |  | 1310 | VAV N°2 min
| 671 | VAV N°2 |  | 927 | VAV N°2 |  | 1288 | VAV N°2 |  |  | MSB | VAV N°2 |  | 671 | VAV N°2 |  | 1055 | VAV N°2 max |  | 1311 | VAV N°2 max
107 | 672 | VAV N°1 | 107 | 928 | VAV N°1 | 107 | 1290 | VAV N°1 | 107 | 1002 | LSB | VAV N°1 | 107 | 672 | VAV N°1 | 54 | 1056 | VAV N°1 min | 118 | 1312 | VAV N°1 min
| 673 | VAV N°2 |  | 929 | VAV N°2 |  | 1291 | VAV N°2 |  |  | MSB | VAV N°2 |  | 673 | VAV N°2 |  | 1057 | VAV N°1 max |  | 1313 | VAV N°1 max
108 | 674 | VAV N°1 | 108 | 930 | VAV N°1 | 108 | 1293 | VAV N°1 | 108 | 1005 | LSB | VAV N°1 | 108 | 674 | VAV N°1 |  | 1058 | VAV N°2 min |  | 1314 | VAV N°2 min
| 675 | VAV N°2 |  | 931 | VAV N°2 |  | 1294 | VAV N°2 |  |  | MSB | VAV N°2 |  | 675 | VAV N°2 |  | 1059 | VAV N°2 max |  | 1315 | VAV N°2 max
109 | 676 | VAV N°1 | 109 | 932 | VAV N°1 | 109 | 1296 | VAV N°1 | 109 | 1008 | LSB | VAV N°1 | 109 | 676 | VAV N°1 | 55 | 1060 | VAV N°1 min | 119 | 1316 | VAV N°1 min
| 677 | VAV N°2 |  | 933 | VAV N°2 |  | 1297 | VAV N°2 |  |  | MSB | VAV N°2 |  | 677 | VAV N°2 |  | 1061 | VAV N°1 max |  | 1317 | VAV N°1 max
110 | 678 | VAV N°1 | 110 | 934 | VAV N°1 | 110 | 1299 | VAV N°1 | 110 | 1011 | LSB | VAV N°1 | 110 | 678 | VAV N°1 |  | 1062 | VAV N°2 min |  | 1318 | VAV N°2 min
| 679 | VAV N°2 |  | 935 | VAV N°2 |  | 1300 | VAV N°2 |  |  | MSB | VAV N°2 |  | 679 | VAV N°2 |  | 1063 | VAV N°2 max |  | 1319 | VAV N°2 max
111 | 680 | VAV N°1 | 111 | 936 | VAV N°1 | 111 | 1302 | VAV N°1 | 111 | 985 | LSB | VAV N°1 | 111 | 680 | VAV N°1 | 56 | 1064 | VAV N°1 min | 120 | 1320 | VAV N°1 min
| 681 | VAV N°2 |  | 937 | VAV N°2 |  | 1303 | VAV N°2 |  |  | MSB | VAV N°2 |  | 681 | VAV N°2 |  | 1065 | VAV N°1 max |  | 1321 | VAV N°1 max
112 | 682 | VAV N°1 | 112 | 938 | VAV N°1 | 112 | 1305 | VAV N°1 | 112 | 988 | LSB | VAV N°1 | 112 | 682 | VAV N°1 |  | 1066 | VAV N°2 min |  | 1322 | VAV N°2 min
| 683 | VAV N°2 |  | 939 | VAV N°2 |  | 1306 | VAV N°2 |  |  | MSB | VAV N°2 |  | 683 | VAV N°2 |  | 1067 | VAV N°2 max |  | 1323 | VAV N°2 max
113 | 684 | VAV N°1 | 113 | 940 | VAV N°1 | 113 | 1308 | VAV N°1 | 113 | 991 | LSB | VAV N°1 | 113 | 684 | VAV N°1 | 57 | 1068 | VAV N°1 min | 121 | 1324 | VAV N°1 min
| 685 | VAV N°2 |  | 941 | VAV N°2 |  | 1309 | VAV N°2 |  |  | MSB | VAV N°2 |  | 685 | VAV N°2 |  | 1069 | VAV N°1 max |  | 1325 | VAV N°1 max
114 | 686 | VAV N°1 | 114 | 942 | VAV N°1 | 114 | 1311 | VAV N°1 | 114 | 994 | LSB | VAV N°1 | 114 | 686 | VAV N°1 |  | 1070 | VAV N°2 min |  | 1326 | VAV N°2 min
| 687 | VAV N°2 |  | 943 | VAV N°2 |  | 1312 | VAV N°2 |  |  | MSB | VAV N°2 |  | 687 | VAV N°2 |  | 1071 | VAV N°2 max |  | 1327 | VAV N°2 max
115 | 688 | VAV N°1 | 115 | 944 | VAV N°1 | 115 | 1314 | VAV N°1 | 115 | 997 | LSB | VAV N°1 | 115 | 688 | VAV N°1 | 58 | 1072 | VAV N°1 min | 122 | 1328 | VAV N°1 min
| 689 | VAV N°2 |  | 945 | VAV N°2 |  | 1315 | VAV N°2 |  |  | MSB | VAV N°2 |  | 689 | VAV N°2 |  | 1073 | VAV N°1 max |  | 1329 | VAV N°1 max
116 | 690 | VAV N°1 | 116 | 946 | VAV N°1 | 116 | 1317 | VAV N°1 | 116 | 1000 | LSB | VAV N°1 | 116 | 690 | VAV N°1 |  | 1074 | VAV N°2 min |  | 1330 | VAV N°2 min
| 691 | VAV N°2 |  | 947 | VAV N°2 |  | 1318 | VAV N°2 |  |  | MSB | VAV N°2 |  | 691 | VAV N°2 |  | 1075 | VAV N°2 max |  | 1331 | VAV N°2 max
117 | 692 | VAV N°1 | 117 | 948 | VAV N°1 | 117 | 1320 | VAV N°1 | 117 | 1003 | LSB | VAV N°1 | 117 | 692 | VAV N°1 | 59 | 1076 | VAV N°1 min | 123 | 1332 | VAV N°1 min
| 693 | VAV N°2 |  | 949 | VAV N°2 |  | 1321 | VAV N°2 |  |  | MSB | VAV N°2 |  | 693 | VAV N°2 |  | 1077 | VAV N°1 max |  | 1333 | VAV N°1 max
118 | 694 | VAV N°1 | 118 | 950 | VAV N°1 | 118 | 1323 | VAV N°1 | 118 | 1006 | LSB | VAV N°1 | 118 | 694 | VAV N°1 |  | 1078 | VAV N°2 min |  | 1334 | VAV N°2 min
| 695 | VAV N°2 |  | 951 | VAV N°2 |  | 1324 | VAV N°2 |  |  | MSB | VAV N°2 |  | 695 | VAV N°2 |  | 1079 | VAV N°2 max |  | 1335 | VAV N°2 max
119 | 696 | VAV N°1 | 119 | 952 | VAV N°1 | 119 | 1326 | VAV N°1 | 119 | 1009 | LSB | VAV N°1 | 119 | 696 | VAV N°1 | 60 | 1080 | VAV N°1 min | 124 | 1336 | VAV N°1 min
| 697 | VAV N°2 |  | 953 | VAV N°2 |  | 1327 | VAV N°2 |  |  | MSB | VAV N°2 |  | 697 | VAV N°2 |  | 1081 | VAV N°1 max |  | 1337 | VAV N°1 max
120 | 698 | VAV N°1 | 120 | 954 | VAV N°1 | 120 | 1329 | VAV N°1 | 120 | 1012 | LSB | VAV N°1 | 120 | 698 | VAV N°1 |  | 1082 | VAV N°2 min |  | 1338 | VAV N°2 min
| 699 | VAV N°2 |  | 955 | VAV N°2 |  | 1330 | VAV N°2 |  |  | MSB | VAV N°2 |  | 699 | VAV N°2 |  | 1083 | VAV N°2 max |  | 1339 | VAV N°2 max
121 | 700 | VAV N°1 | 121 | 956 | VAV N°1 | 121 | 1332 | VAV N°1 | 121 | 986 | LSB | VAV N°1 | 121 | 700 | VAV N°1 | 61 | 1084 | VAV N°1 min | 125 | 1340 | VAV N°1 min
| 701 | VAV N°2 |  | 957 | VAV N°2 |  | 1333 | VAV N°2 |  |  | MSB | VAV N°2 |  | 701 | VAV N°2 |  | 1085 | VAV N°1 max |  | 1341 | VAV N°1 max
122 | 702 | VAV N°1 | 122 | 958 | VAV N°1 | 122 | 1335 | VAV N°1 | 122 | 989 | LSB | VAV N°1 | 122 | 702 | VAV N°1 |  | 1086 | VAV N°2 min |  | 1342 | VAV N°2 min
| 703 | VAV N°2 |  | 959 | VAV N°2 |  | 1336 | VAV N°2 |  |  | MSB | VAV N°2 |  | 703 | VAV N°2 |  | 1087 | VAV N°2 max |  | 1343 | VAV N°2 max
123 | 704 | VAV N°1 | 123 | 960 | VAV N°1 | 123 | 1338 | VAV N°1 | 123 | 992 | LSB | VAV N°1 | 123 | 704 | VAV N°1 | 62 | 1088 | VAV N°1 min | 126 | 1344 | VAV N°1 min
| 705 | VAV N°2 |  | 961 | VAV N°2 |  | 1339 | VAV N°2 |  |  | MSB | VAV N°2 |  | 705 | VAV N°2 |  | 1089 | VAV N°1 max |  | 1345 | VAV N°1 max
124 | 706 | VAV N°1 | 124 | 962 | VAV N°1 | 124 | 1341 | VAV N°1 | 124 | 995 | LSB | VAV N°1 | 124 | 706 | VAV N°1 |  | 1090 | VAV N°2 min |  | 1346 | VAV N°2 min
| 707 | VAV N°2 |  | 963 | VAV N°2 |  | 1342 | VAV N°2 |  |  | MSB | VAV N°2 |  | 707 | VAV N°2 |  | 1091 | VAV N°2 max |  | 1347 | VAV N°2 max
125 | 708 | VAV N°1 | 125 | 964 | VAV N°1 | 125 | 1344 | VAV N°1 | 125 | 998 | LSB | VAV N°1 | 125 | 708 | VAV N°1 | 63 | 1092 | VAV N°1 min | 127 | 1348 | VAV N°1 min
| 709 | VAV N°2 |  | 965 | VAV N°2 |  | 1345 | VAV N°2 |  |  | MSB | VAV N°2 |  | 709 | VAV N°2 |  | 1093 | VAV N°1 max |  | 1349 | VAV N°1 max
126 | 710 | VAV N°1 | 126 | 966 | VAV N°1 | 126 | 1347 | VAV N°1 | 126 | 1001 | LSB | VAV N°1 | 126 | 710 | VAV N°1 |  | 1094 | VAV N°2 min |  | 1350 | VAV N°2 min
| 711 | VAV N°2 |  | 967 | VAV N°2 |  | 1348 | VAV N°2 |  |  | MSB | VAV N°2 |  | 711 | VAV N°2 |  | 1095 | VAV N°2 max |  | 1351 | VAV N°2 max
127 | 712 | VAV N°1 | 127 | 968 | VAV N°1 | 127 | 1350 | VAV N°1 | 127 | 1004 | LSB | VAV N°1 | 127 | 712 | VAV N°1 | 64 | 1096 | VAV N°1 min | 128 | 1352 | VAV N°1 min
| 713 | VAV N°2 |  | 969 | VAV N°2 |  | 1351 | VAV N°2 |  |  | MSB | VAV N°2 |  | 713 | VAV N°2 |  | 1097 | VAV N°1 max |  | 1353 | VAV N°1 max
128 | 714 | VAV N°1 | 128 | 970 | VAV N°1 | 128 | 1353 | VAV N°1 | 128 | 1007 | LSB | VAV N°1 | 128 | 714 | VAV N°1 |  | 1098 | VAV N°2 min |  | 1354 | VAV N°2 min
| 715 | VAV N°2 |  | 971 | VAV N°2 |  | 1354 | VAV N°2 |  |  | MSB | VAV N°2 |  | 715 | VAV N°2 |  | 1099 | VAV N°2 max |  | 1355 | VAV N°2 max

## EASY-ECO
Easy-ECO (EnOcéan) | [12 empty] | A = Input 1
B = Input 2
C = Input 3
D = Input 4
E = Input 5
Easybus | modbus RTU | [8 empty] | Easybus | modbus RTU |  | F = Input 6
Adress |  | Read (bits) | [7 empty] | Address |  | Read (bits) | G = Input 7
|  | H | G | F | E | D | C | B | A |  |  | Module error communication | H = Input 8
1 | 365 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 1 | 300 | 0
2 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 2 |  | 4
3 | 366 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 3 |  | 8
4 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 4 |  | 12
5 | 367 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 5 | 301 | 0
6 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 6 |  | 4
7 | 368 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 7 |  | 8
8 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 8 |  | 12
9 | 369 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 9 | 302 | 0
10 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 10 |  | 4
11 | 370 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 11 |  | 8
12 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 12 |  | 12
13 | 371 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 13 | 303 | 0
14 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 14 |  | 4
15 | 372 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 15 |  | 8
16 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 16 |  | 12
17 | 373 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 17 | 304 | 0
18 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 18 |  | 4
19 | 374 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 19 |  | 8
20 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 20 |  | 12
21 | 375 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 21 | 305 | 0
22 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 22 |  | 4
23 | 376 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 23 |  | 8
24 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 24 |  | 12
25 | 377 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 25 | 306 | 0
26 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 26 |  | 4
27 | 378 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 27 |  | 8
28 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 28 |  | 12
29 | 379 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 29 | 307 | 0
30 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 30 |  | 4
31 | 380 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 31 |  | 8
32 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 32 |  | 12
33 | 381 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 33 | 308 | 0
34 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 34 |  | 4
35 | 382 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 35 |  | 8
36 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 36 |  | 12
37 | 383 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 37 | 309 | 0
38 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 38 |  | 4
39 | 384 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 39 |  | 8
40 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 40 |  | 12
41 | 385 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 41 | 310 | 0
42 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 42 |  | 4
43 | 386 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 43 |  | 8
44 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 44 |  | 12
45 | 387 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 45 | 311 | 0
46 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 46 |  | 4
47 | 388 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 47 |  | 8
48 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 48 |  | 12
49 | 389 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 49 | 312 | 0
50 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 50 |  | 4
51 | 390 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 51 |  | 8
52 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 52 |  | 12
53 | 391 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 53 | 313 | 0
54 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 54 |  | 4
55 | 392 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 55 |  | 8
56 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 56 |  | 12
57 | 393 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 57 | 314 | 0
58 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 58 |  | 4
59 | 394 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 59 |  | 8
60 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 60 |  | 12
61 | 395 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 61 | 315 | 0
62 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 62 |  | 4
63 | 396 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 63 |  | 8
64 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 64 |  | 12
65 | 397 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 65 | 316 | 0
66 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 66 |  | 4
67 | 398 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 67 |  | 8
68 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 68 |  | 12
69 | 399 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 69 | 317 | 0
70 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 70 |  | 4
71 | 400 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 71 |  | 8
72 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 72 |  | 12
73 | 401 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 73 | 318 | 0
74 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 74 |  | 4
75 | 402 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 75 |  | 8
76 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 76 |  | 12
77 | 403 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 77 | 319 | 0
78 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 78 |  | 4
79 | 404 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 79 |  | 8
80 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 80 |  | 12
81 | 405 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 81 | 320 | 0
82 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 82 |  | 4
83 | 406 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 83 |  | 8
84 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 84 |  | 12
85 | 407 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 85 | 321 | 0
86 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 86 |  | 4
87 | 408 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 87 |  | 8
88 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 88 |  | 12
89 | 409 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 89 | 322 | 0
90 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 90 |  | 4
91 | 410 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 91 |  | 8
92 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 92 |  | 12
93 | 411 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 93 | 323 | 0
94 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 94 |  | 4
95 | 412 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 95 |  | 8
96 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 96 |  | 12
97 | 413 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 97 | 324 | 0
98 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 98 |  | 4
99 | 414 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 99 |  | 8
100 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 100 |  | 12
101 | 415 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 101 | 325 | 0
102 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 102 |  | 4
103 | 416 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 103 |  | 8
104 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 104 |  | 12
105 | 417 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 105 | 326 | 0
106 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 106 |  | 4
107 | 418 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 107 |  | 8
108 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 108 |  | 12
109 | 419 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 109 | 327 | 0
110 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 110 |  | 4
111 | 420 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 111 |  | 8
112 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 112 |  | 12
113 | 421 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 113 | 328 | 0
114 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 114 |  | 4
115 | 422 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 115 |  | 8
116 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 116 |  | 12
117 | 423 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 117 | 329 | 0
118 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 118 |  | 4
119 | 424 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 119 |  | 8
120 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 120 |  | 12
121 | 425 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 121 | 330 | 0
122 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 122 |  | 4
123 | 426 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 123 |  | 8
124 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 124 |  | 12
125 | 427 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 125 | 331 | 0
126 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 126 |  | 4
127 | 428 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | 127 |  | 8
128 |  | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 128 |  | 12